## FrontPage
Electricity storage and renewables: Costs and markets to 2030
Cost-of-service tool. Version 1.0

## Instructions
Instructions
The purpose of this tool is to assist you in determining the cost-of-service of different storage technologies.
This sheet provides step-by-step instruction on how to utilise it.
|  | Contact information: | costs@irena.org
Disclaimer
This tool is based on data which were compiled from over 150 data sources, supplemented by expert interviews and analysis by IRENA of the latest battery developments.
As a result, this data is a blend of different analytical approaches, including data from: installed projects, regulatory databases, installer surveys, individual projects, bottom-up engineering analyses and learning curve studies.
Given the rapidly changing market place for electricity storage and the difficulty in always obtaining up-to-date data for each technology, the results should be treated with caution.
The methodology of the calculations is explained in Annex 2 of the report which can be downloaded from:
http://www.irena.org/DocumentDownloads/Publications/IRENA_Electricity_Storage_Costs_2017.pdf
Step 1
Select the 'Cost of Service' sheet.
Select the storage technology option that you wish to evaluate:
Step 2
Select the Power conversion unit to evaluate:
Note: After you have changed the energy storage unit choice the first time, you may need to adjust the power conversion unit choice again, from those available in the dropdown.
Step 3
Select the application type to evaluate:
Note: The tool contains 12 predefined storage applications, which can be chosen from this dropdown menu. However, in the 'Applications' sheet, you can modify their parameters.
You can also create new ones (see also "Applications: Modifying parameters or creating new applications" section at the end of this sheet).
Step 4
If available, you can add additional information on local conditions:
Note: The tool assumes the same value you input would apply for all cases in each period.
Results: Key results
The tool displays results for major calculation steps and also displays a summary of the results as shown below:
Results: Technology Development (Results Summary and Visualisation)
The tool contains charts to visualise the key results and provides a summarized table of cost-of-services estimates for the selected technology and application combination evaluated.
You can toggle between the cost-of service type ("electricity" or "power" options). The charts displaying the composition of the annuities (left) and the cost-of-service development will update accordingly.
Results: Technology Comparison Chart (to place results of various runs)
The tool provides a section where you can store some of the runs of estimates that you have done and in this way compare different technology options. It also charts these so you can visualise them automatically.
Applications: Modifying parameters or creating new applications
In the 'Applications' sheet, the tool provides a section where you can modify the 12 predefined storage applications altering their key parameters. You also have the option to define your own applications defining them by these parameters.
If you add additional applications to the 'Applications' sheet, they will appear as an option in the 'Cost-of-Service' sheet (see Step 3 of these instructions).

## Cost-of-Service
Energy Storage Unit
| Energy Storage Unit | 2016 |  |  | 2020 |  |  | 2025 |  |  | 2030
Choose ---> | Li-Ion (LFP) | best | worst | reference | best | worst | reference | best | worst | reference | best | worst | reference | unit
X | Energy density | 620 | 200 | 350 | 620 | 200 | 350 | 620 | 200 | 350 | 620 | 200 | 350 | Wh/l
X | Power density | 10000 | 100 | 3500 | 10000 | 100 | 3500 | 10000 | 100 | 3500 | 10000 | 100 | 3500 | W/l
| Cycle life | 10000 | 1000 | 2500 | 12030.2906 | 1203.0291 | 3007.5727 | 15157.2798 | 1515.728 | 3789.32 | 19097.0558 | 1909.7056 | 4774.264 | equivalent full-cycles
| Calendar life | 20 | 5 | 12 | 22.5912 | 5.6478 | 13.5547 | 26.3073 | 6.5768 | 15.7844 | 30.6348 | 7.6587 | 18.3809 | a
| Depth of discharge | 100 | 84 | 90 | 100 | 84 | 90 | 100 | 84 | 90 | 100 | 84 | 90 | %
| Round-trip efficiency | 94 | 81 | 92 | 94.4927 | 81.4246 | 92.4822 | 95.1122 | 81.9584 | 93.0886 | 95.7358 | 82.4957 | 93.6989 | %
| Self-discharge | 0.09 | 0.36 | 0.1 | 0.09 | 0.36 | 0.1 | 0.09 | 0.36 | 0.1 | 0.09 | 0.36 | 0.1 | % per day
X | Power dynamic | 0.003 | 1 | 0.01 | 0.003 | 1 | 0.01 | 0.003 | 1 | 0.01 | 0.003 | 1 | 0.01 | s to rated power
X | Planning & Construction Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | a
| Energy installation cost | 199.5 | 840 | 577.5 | 152.2242 | 640.9439 | 440.6489 | 108.5574 | 457.0839 | 314.2452 | 77.4168 | 325.9656 | 224.1014 | USD / kWh
| Power installation cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | USD / kW
Power Conversion Unit
| Power Conversion Unit | 2016 |  |  | 2020 |  |  | 2025 |  |  | 2030
Choose ---> | Inverter large | best | worst | reference | best | worst | reference | best | worst | reference | best | worst | reference | unit
x | Energy density | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | Wh/l
x | Power density | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0 | 0 | 0.15 | W/l
x | Cycle life | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | equivalent full-cycles
| Calendar life | 25 | 12 | 15 | 25 | 13.4369 | 16.7961 | 25 | 15.4772 | 19.3466 | 25 | 17.8275 | 22.2843 | a
X | Depth of discharge | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | %
| Round-trip efficiency | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | %
x | Self-discharge | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | % per day
x | Power dynamic | - | - | 0.02 | 0 | 0 | 0.02 | 0 | 0 | 30 | 0 | 0 | 30 | s to rated power
x | Planning & Construction Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 0 | 0 | - | a
| Energy installation cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | USD / kWh
| Power installation cost | 73.5 | 189 | 105 | 59.6483 | 153.3814 | 85.2119 | 45.9449 | 118.1439 | 65.6355 | 35.3896 | 91.0018 | 50.5566 | USD / kW
Application
| Application | 2016 |  |  | 2020 |  |  | 2025 |  |  | 2030
Choose ---> | Peak shaving | best | worst | reference | best | worst | reference | best | worst | reference | best | worst | reference | unit
| Power | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | kW
| E/P Ratio | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | h
| Cycles per day | 0.054795 | 0.054795 | 0.054795 | 0.054795 | 0.054795 | 0.054795 | 0.054795 | 0.054795 | 0.054795 | 0.054795 | 0.054795 | 0.054795 | -
| Electricity price [USDcents / kWh] | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | USDcents / kWh
Country-specific data
| Country-specific data | 2016 |  |  | 2020 |  |  | 2025 |  |  | 2030
| Add additional data below if available | best | worst | reference | best | worst | reference | best | worst | reference | best | worst | reference | unit
| Maintenance storage system | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | % of invest per year
| Maintenance power conversion unit | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | % of invest per year
| Interest rate | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | %
| Other fixed costs (upfront) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | USD
| Other fixed costs (yearly) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | USD per year
Calculations
| Calculations | 2016 |  |  | 2020 |  |  | 2025 |  |  | 2030
|  | best | worst | reference | best | worst | reference | best | worst | reference | best | worst | reference | unit
Energy Storage Unit
| Installed Storage Power | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | kW
| Usable Storage Capacity | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | kWh
| Installed Storage Capacity | 60 | 71.4286 | 66.6667 | 60 | 71.4286 | 66.6667 | 60 | 71.4286 | 66.6667 | 60 | 71.4286 | 66.6667 | kWh
| Lifetime in application | 20 | 5 | 12 | 22.5912 | 5.6478 | 13.5547 | 26.3073 | 6.5768 | 15.7844 | 30.6348 | 7.6587 | 18.3809 | a
| Total Storage Invest | 11970 | 60000 | 38500 | 9133.4503 | 45781.7057 | 29376.5945 | 6513.4453 | 32648.8484 | 20949.6778 | 4645.0101 | 23283.2589 | 14940.0911 | USD
| Annuities Energy Storage Unit | 781.1379 | 12719.6838 | 3755.1362 | 546.0812 | 8672.738 | 2591.8459 | 350.9943 | 5382.4311 | 1636.5459 | 227.1246 | 3347.4783 | 1038.0919 | USD
Power Conversion Unit
| Installed Conversion Power | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | kW
| Total Conversion Invest | 14700 | 37800 | 21000 | 11929.6662 | 30676.2844 | 17042.3802 | 9188.9732 | 23628.7883 | 13127.1046 | 7077.9205 | 18200.367 | 10111.315 | USD
| Annuities Power Conversion Unit | 819.6017 | 3686.861 | 1707.8623 | 665.1411 | 2725.8208 | 1268.4576 | 512.3332 | 1874.5921 | 877.8877 | 394.631 | 1294.2027 | 610.4032 | USD
Total Investment
| Energy Storage + Power Conversion | 26670 | 97800 | 59500 | 21063.1165 | 76457.9901 | 46418.9747 | 15702.4185 | 56277.6367 | 34076.7823 | 11722.9306 | 41483.6259 | 25051.4061 | USD
| Total Invest per usable kWh storage | 444.5 | 1630 | 991.6667 | 351.0519 | 1274.2998 | 773.6496 | 261.707 | 937.9606 | 567.9464 | 195.3822 | 691.3938 | 417.5234 | USD
Energy losses
| Energy throughput per year | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | kWh
| Total efficiency | 92.12 | 79.38 | 90.16 | 92.6029 | 79.7961 | 90.6326 | 93.21 | 80.3192 | 91.2268 | 93.8211 | 80.8458 | 91.8249 | %
| Efficiency losses [kWh] | 102.6487 | 311.7158 | 130.9672 | 95.8564 | 303.8333 | 124.0272 | 87.4158 | 294.0381 | 115.4031 | 79.0301 | 284.3066 | 106.8351 | kWh
| Efficiency losses [USD] | 18.4768 | 56.1088 | 23.5741 | 17.2542 | 54.69 | 22.3249 | 15.7348 | 52.9269 | 20.7726 | 14.2254 | 51.1752 | 19.2303 | USD
| Self-discharge losses [kWh] | 19.71 | 93.8571 | 24.3333 | 19.71 | 93.8571 | 24.3333 | 19.71 | 93.8571 | 24.3333 | 19.71 | 93.8571 | 24.3333 | kWh
| Self-discharge losses [USD] | 3.5478 | 16.8943 | 4.38 | 3.5478 | 16.8943 | 4.38 | 3.5478 | 16.8943 | 4.38 | 3.5478 | 16.8943 | 4.38 | USD
Annuities
| Annuities Invest | 1600.7395 | 16406.5448 | 5462.9985 | 1211.2223 | 11398.5588 | 3860.3035 | 863.3275 | 7257.0232 | 2514.4335 | 621.7556 | 4641.6811 | 1648.4951 | USD
| Capital | 1186.5 | 15150 | 4608.3333 | 881.4786 | 10389.0985 | 3181.9213 | 615.1493 | 6490.897 | 2005.763 | 434.7423 | 4061.0289 | 1266.5488 | USD
| Financing | 414.2395 | 1256.5448 | 854.6652 | 329.7437 | 1009.4603 | 678.3822 | 248.1782 | 766.1262 | 508.6706 | 187.0132 | 580.6521 | 381.9463 | USD
| Maintenance | 400.05 | 1467 | 892.5 | 315.9467 | 1146.8699 | 696.2846 | 235.5363 | 844.1646 | 511.1517 | 175.844 | 622.2544 | 375.7711 | USD
| Efficiency losses | 18.4768 | 56.1088 | 23.5741 | 17.2542 | 54.69 | 22.3249 | 15.7348 | 52.9269 | 20.7726 | 14.2254 | 51.1752 | 19.2303 | USD
| Self-discharge | 3.5478 | 16.8943 | 4.38 | 3.5478 | 16.8943 | 4.38 | 3.5478 | 16.8943 | 4.38 | 3.5478 | 16.8943 | 4.38 | USD
| Sum | 2022.8141 | 17946.5479 | 6383.4526 | 1547.971 | 12617.013 | 4583.293 | 1118.1464 | 8171.0089 | 3050.7378 | 815.3728 | 5332.0049 | 2047.8765 | USD
| Calculations -key results | 2016 |  |  | 2020 |  |  | 2025 |  |  | 2030
| Levelised cost-of-service | best | worst | reference | best | worst | reference | best | worst | reference | best | worst | reference | unit
Results --> | Cost per kW storage system per year [USD] | 10.1141 | 89.7327 | 31.9173 | 7.7399 | 63.0851 | 22.9165 | 5.5907 | 40.855 | 15.2537 | 4.0769 | 26.66 | 10.2394 | USD
Results --> | Cost per kWh stored electricity [USD] | 1.6857 | 14.9555 | 5.3195 | 1.29 | 10.5142 | 3.8194 | 0.93179 | 6.8092 | 2.5423 | 0.67948 | 4.4433 | 1.7066 | USD
Technology Development (Results Summary and Visualisation)
Cost-of-service type
Choose ---> | Power
|  | Peak shaving | [6 empty] | Suitable: | OK | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| Li-Ion (LFP) | 2016 | 2020 | 2025 | 2030 | Unit |  | Cost-of-service, Li-Ion (LFP) — Peak shaving | Validity check: | OK | 1 | 1 | 1
| Best | 10.1141 | 7.7399 | 5.5907 | 4.0769 | USD per kW
| Worst | 89.7327 | 63.0851 | 40.855 | 26.66 | USD per kW
| Reference | 31.9173 | 22.9165 | 15.2537 | 10.2394 | USD per kW
Technology Comparison Chart (to place results of various runs)
1. Current selected reference case values are shown below
|  | 2016 | 2020 | 2025 | 2030 | Unit
| Li-Ion (LFP) | 31.9173 | 22.9165 | 15.2537 | 10.2394 | USD per kW
2. You can copy results into table to form your own calculations history that will be displayed in the chart to the right
| Peak shaving | 2016 | 2020 | 2025 | 2030 | Unit |  |  |  |  | Validity check: | OK
| Flywheel | 123.1751 | 96.7599 | 78.4638 | 64.0031 | USD per kW
| Li-Ion (LFP) | 31.9173 | 22.9165 | 15.2537 | 10.2394 | USD per kW
| NaS | 20.2053 | 15.1674 | 10.6535 | 7.5289 | USD per kW

## Dropdowns (hidden)
Pumped Hydro | CAES | Flywheel | Flooded LA | VRLA | Li-Ion (LFP) | Li-Ion (NCA) | Li-Ion (NMC) | Li-Ion (Titanate) | NaNiCl | NaS | Vanadium Flow | ZnBr Flow
Generator PHS | Generator CAES | Generator Flywheel | Inverter small | Inverter small | Inverter small | Inverter small | Inverter small | Inverter small | Inverter small | Inverter small | Inverter small | Inverter small
|  |  | Inverter large | Inverter large | Inverter large | Inverter large | Inverter large | Inverter large | Inverter large | Inverter large | Inverter large | Inverter large
|  |  | No inverter | No inverter | No inverter | No inverter | No inverter | No inverter | No inverter | No inverter | No inverter | No inverter

## Applications
| [kW] | [kWh/kW] | [N/day] | [USDcents/kWh]
Applications | Power | E/P Ratio | Cycles per day | Electricity price | Comment
Enhanced Frequency Respose | 5000 | 1 | 1 | 3 | Typical 5MW design comparable to WEMAG or M5BATT
Frequency Containment Reserve | 5000 | 1.33 | 1 | 3 | Typical 5MW design comparable to WEMAG or M5BATT
Frequency Restoration Reserve | 15000 | 2 | 0.5 | 3
Energy shifting | 1060000 | 8.0189 | 0.8 | 3 | Largest PHS in Germany: Goldisthal, operational since 1991
Self-consumption (small residential) | 2.5 | 2 | 0.60274 | 29 | Typical PV Battery System in Germany
Community storage | 224 | 0.85429 | 1 | 29 | EnergyNeighbor research project
Increase Power Quality | 12 | 2 | 0.1 | 29
Peak shaving | 200 | 0.3 | 0.054795 | 18
Time-of-use | 5 | 4 | 1 | 20
Nano Offgrid | 0.2 | 2 | 0.85 | 100 | Small hut with 200W PV
Village electrification | 50 | 2.5 | 0.9 | 100 | Small village in Columbia
Island grid | 800 | 3.5 | 1 | 100 | Greek island Tilos: 2x 400 kWh ZEBRA battery used for RE integration
Insert more applications as needed here in the blank rows of the table. You can also modify parameters of predefined ones.

## List of Storage Technologies (hidden)
Pumped Hydro
CAES
Flywheel
Flooded LA
VRLA
Li-Ion (LFP)
Li-Ion (NCA)
Li-Ion (NMC)
Li-Ion (Titanate)
NaNiCl
NaS
Vanadium Flow
ZnBr Flow
<-- If new storage technologies are added, reference them here

## Overview 2016 (in) (hidden)
Mechanical
| Pumped Hydro |  |  | CAES |  |  | Flywheel
| best | worst | reference | best | worst | reference | best | worst | reference | unit
Energy density | 2 | 0.2 | 1 | 6 | 2 | 3 | 200 | 20 | 80 | Wh/l | dollar/euro conversion
Power density | 0.2 | 0.1 | 0.15 | 0.6 | 0.2 | 0.4 | 10000 | 5000 | 7500 | W/l | 1.05 |  | 2017-01-02
Cycle life | 100000 | 12000 | 50000 | 100000 | 10000 | 50000 | 1000000 | 100000 | 200000 | equivalent full-cycles
Calendar life | 100 | 30 | 60 | 100 | 20 | 50 | 25 | 15 | 20 | a | ,0- | €-Format | 1
Depth of discharge | 100 | 80 | 90 | 50 | 35 | 40 | 90 | 75 | 85 | % | ,0 | $-Format | 1 $
Round-trip efficiency | 84 | 70 | 80 | 75 | 40 | 60 | 99 | 70 | 84 | %
Self-discharge | 0 | 0.02 | 0.01 | 0 | 1 | 0.5 | 20 | 100 | 60 | % per day
Power dynamic | 15 | 500 | 30 | sec | 900 | 480 | < 0,004 | sec | 0.05 | s to rated power
Planning & Construction Time | 5 | 25 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | a
Energy installation cost | 5.25 | 100 | 21 | 2 | 84 | 52.5 | 1500 | 6000 | 3000 | USD / kWh
Power installation cost | 525 | 2000 | 840 | 400 | 1050 | 945 | 315 | 1050 | 300 | USD / kW
| Lead-Acid | [5 empty] | Li-Ion
| Flooded LA |  |  | VRLA |  |  | NMC/LMO
| best | worst | ref | best | worst | ref | best | worst | ref | unit
Energy density | 100 | 50 | 80 | 100 | 50 | 80 | 735 | 200 | 468 | Wh/l
Power density | 700 | 10 | 350 | 700 | 10 | 350 | 10000 | 100 | 3500 | W/l
Cycle life | 2500 | 250 | 1500 | 2500 | 250 | 1500 | 4000 | 500 | 2000 | equivalent full-cycles
Calendar life | 15 | 3 | 9 | 15 | 3 | 9 | 20 | 5 | 12 | a
Depth of discharge | 50 | 60 | 50 | 50 | 60 | 50 | 100 | 84 | 90 | %
Round-trip efficiency | 92 | 75 | 82 | 92 | 75 | 80 | 98 | 81 | 95 | %
Self-discharge | 0.09 | 0.4 | 0.25 | 0.09 | 0.4 | 0.25 | 0.09 | 0.36 | 0.1 | % per day
Power dynamic | 0.003 | 0.01 | 0.006 | 0.003 | 0.01 | 0.006 | 0.003 | 1 | 0.01 | s to rated power
Planning & Construction Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | a
Energy installation cost | 105 | 472.5 | 147 | 105 | 472.5 | 262.5 | 199.5 | 840 | 420 | USD / kWh
Power installation cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | USD / kW
Li-Ion
| NCA |  |  | LiFePo4 |  |  | Titanate
| best | worst | reference | best | worst | reference | best | worst | reference | unit
Energy density | 620 | 200 | 350 | 620 | 200 | 350 | 620 | 200 | 350 | Wh/l
Power density | 10000 | 100 | 3500 | 10000 | 100 | 3500 | 10000 | 100 | 3500 | W/l
Cycle life | 2000 | 500 | 1000 | 10000 | 1000 | 2500 | 20000 | 5000 | 10000 | equivalent full-cycles
Calendar life | 20 | 5 | 12 | 20 | 5 | 12 | 20 | 10 | 15 | a
Depth of discharge | 100 | 84 | 90 | 100 | 84 | 90 | 100 | 84 | 95 | %
Round-trip efficiency | 98 | 81 | 95 | 94 | 81 | 92 | 98 | 81 | 96 | %
Self-discharge | 0.09 | 0.36 | 0.2 | 0.09 | 0.36 | 0.1 | 0.09 | 0.36 | 0.05 | % per day
Power dynamic | 0.003 | 1 | 0.01 | 0.003 | 1 | 0.01 | 0.003 | 1 | 0.01 | s to rated power
Planning & Construction Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | a
Energy installation cost | 199.5 | 840 | 351.75 | 199.5 | 840 | 577.5 | 472.5 | 1260 | 1050 | USD / kWh
Power installation cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | USD / kW
| High Temperature | [5 empty] | Flow
| NaNiCl |  |  | NaS |  |  | Vanadium
| best | worst | reference | best | worst | reference | best | worst | reference | unit
Energy density | 280 | 150 | 215 | 300 | 140 | 250 | 70 | 15 | 45 | Wh/l
Power density | 270 | 150 | 210 | 160 | 120 | 140 | 2 | 0.5 | 1.3 | W/l
Cycle life | 7500 | 1000 | 3000 | 10000 | 1000 | 5000 | 14000 | 12000 | 13000 | equivalent full-cycles
Calendar life | 22 | 8 | 15 | 25 | 10 | 17 | 20 | 5 | 12 | a
Depth of discharge | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | %
Round-trip efficiency | 92 | 80 | 84 | 90 | 70 | 80 | 85 | 60 | 70 | %
Self-discharge | 0.05 | 15 | 5 | 0.05 | 1 | 0.05 | 0 | 1 | 0.15 | % per day
Power dynamic | 0.1 | < 1 | 0.5 | 3 | 20 | 10 | < 0.001 | 0.02 | 0.01 | s to rated power
Planning & Construction Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | a
Energy installation cost | 315 | 488 | 399 | 262.5 | 735 | 367.5 | 315 | 1050 | 346.5 | USD / kWh
Power installation cost | 0 | 0 | 0 | 0 | 0 | 0 | 1050 | 1575 | 1312.5 | USD / kW
| Flow |  |  | Inverter
| Zn/Br |  |  | Small (1-30kW) |  |  | Large (>30kW)
| best | worst | ref | best | worst | ref | best | worst | ref | unit
Energy density | 70 | 20 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | Wh/l
Power density | 25 | 0.5 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | W/l
Cycle life | 14000 | 300 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | equivalent full-cycles
Calendar life | 20 | 5 | 10 | 25 | 10 | 12 | 25 | 12 | 15 | a
Depth of discharge | 100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | %
Round-trip efficiency | 85 | 60 | 70 | 97 | 93 | 95 | 98 | 98 | 98 | %
Self-discharge | 8 | 33.6 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | % per day
Power dynamic | < 0.001 | 0.02 | 0.01 | - | - | 0.02 | - | - | 0.02 | s to rated power
Planning & Construction Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | a
Energy installation cost | 525 | 1680 | 900 | 0 | 0 | 0 | 0 | 0 | 0 | USD / kWh
Power installation cost | 0 | 0 | 0 | 105 | 290 | 155.4 | 73.5 | 189 | 105 | USD / kW

## Pumped Hydro (calc) (hidden)
| Pumped Hydro | [6 empty] | Sources
|  | 2016 | 2020 | 2025 | 2030 | unit |  | Source 2016 | Source 2020 | Source 2025 | Source 2030
| Energy installation cost | 21 | 21 | 21 | 21 | USD / kWh |  | 2016 | combination | combination | combination
| Power installation cost | 840 | 840 | 840 | 840 | USD / kW |  | 2016 | combination | combination | combination
| Cycle life | 50000 | 50000 | 50000 | 50000 | equivalent full-cycles |  | 2016 | combination | combination | combination
| Calendar life | 60 | 60 | 60 | 60 | a |  | 2016 | combination | combination | combination
| Round-trip efficiency | 80 | 80 | 80 | 80 | % |  | 2016 | combination | combination | combination
interpolated
| References | [8 empty] | extrapolated
| Number of Source | Titel | Authors | Web | Date |  |  |  |  | not needed or not available
| 1 | Technology Overview on Electricity Storage | Fuchs, Lunz, Leuthold, Sauer | http://www.sefep.eu/activities/projects-studies/120628_Technology_Overview_Electricity_Storage_SEFEP_ISEA.pdf | June 2012
| 2 | Agora Stromspeicher in der Energiewende | Agora Energiewende | http://www.speicherinitiative.at/assets/Uploads/19-AgoraEnergiewende-Speicherstudie-Langfassung.pdf | September 2014
| 3 | Energiesysteme der Zukunft - Technologiesteckbrief Energiespeicher | Prof. Dr. Peter Elsner, Prof. Dr. Dirk Uwe Sauer | http://www.acatech.de/fileadmin/user_upload/Baumstruktur_nach_Website/Acatech/root/de/Publikationen/Materialien/ESYS_Technologiesteckbrief_Energiespeicher.pdf | November 2015
Percental
Interpolation |  | ref | source
Source 1 |  | 2016 | 2012 | 2020 | 2023 | 2025 | 2030 | 2033 | unit | X1 | X2 | SEFEP does not expect any improvement/cost reduction of Pumped Hydro
| Energy installation cost | 20 | 12.5 | 12.5 |  | 12.5 | 12.5 |  | USD / kWh | 0
| Power installation cost | 800 | 750 | 750 |  | 750 | 750 |  | USD / kW | 0
| Cycle life | 50000 | 9999999 | 9999999 |  | 9999999 | 9999999 |  | equivalent full-cycles | 0
| Calendar life | 80 | 80 | 80 |  | 80 | 80 |  | a | 0
| Round-trip efficiency | 80 | 78.5 | 78.5 |  | 78.5 | 78.5 |  | % | 0
Source 2 |  | 2016 | 2014 | 2020 | 2023 | 2025 | 2030 | 2050 | unit |  |  | Instead of years, the Agora study refers to shares of renewable energies (see below). Therefore, respective assumptions were made.
| Energy installation cost | 50 | 30 | 50 | 50 | 50 | 50 | 50 | USD / kWh | 0 | 0
| Power installation cost | 1000 | 1025 | 1000 | 1000 | 1000 | 1000 | 1000 | USD / kW |  |  | @ Jan - Die Agora Studie bitte erstmal nicht nutzen, da muss ich mir noch was überlegen
| Cycle life | 50000 | 9999999 | [5 empty] | equivalent full-cycles
| Calendar life | 60 | 60 | 60 | 60 | 60 | 60 | 60 | a | 0 | 0
| Round-trip efficiency | 80 | 80 | 80 | 80 | 80 | 80 | 80 | % | 0 | 0
Source 3 |  | 2016 | 2015 | 2020 | 2023 | 2025 | 2030 | 2050 | unit
| Energy installation cost | 50 | 78.3 |  |  |  |  | 50 | USD / kWh | 0
| Power installation cost | 850 | [5 empty] | 850 | USD / kW | 0
| Cycle life | 100000 |  | 100000 | 100000 | 100000 | 100000 | 100000 | equivalent full-cycles | 0
| Calendar life | 60 |  | 62.0655 | 63.6611 | 64.7475 | 67.5455 | 80 | a | -0.0084971
| Round-trip efficiency | 80 |  | 80 | 80 | 80 | 80 | 80 | % | 0

## Pumped Hydro (hidden)
| 2016 |  |  | 2020 |  |  | 2025 |  |  | 2030
Pumped Hydro (calc) | best | worst | reference | best | worst | reference | best | worst | reference | best | worst | reference | unit
Energy density | 2 | 0.2 | 1 | 2 | 0.2 | 1 | 2 | 0.2 | 1 | 2 | 0.2 | 1 | Wh/l
Power density | 0.2 | 0.1 | 0.15 | 0.2 | 0.1 | 0.15 | 0.2 | 0.1 | 0.15 | 0.2 | 0.1 | 0.15 | W/l
Cycle life | 100000 | 12000 | 50000 | 100000 | 12000 | 50000 | 100000 | 12000 | 50000 | 100000 | 12000 | 50000 | equivalent full-cycles
Calendar life | 100 | 30 | 60 | 100 | 30 | 60 | 100 | 30 | 60 | 100 | 30 | 60 | a
Depth of discharge | 100 | 80 | 90 | 100 | 80 | 90 | 100 | 80 | 90 | 100 | 80 | 90 | %
Round-trip efficiency | 84 | 70 | 80 | 84 | 70 | 80 | 84 | 70 | 80 | 84 | 70 | 80 | %
Self-discharge | 0 | 0.02 | 0.01 | 0 | 0.02 | 0.01 | 0 | 0.02 | 0.01 | 0 | 0.02 | 0.01 | % per day
Power dynamic | 15 | 500 | 30 | 15 | 500 | 30 | 15 | 500 | 30 | 15 | 500 | 30 | s to rated power
Planning & Construction Time | 5 | 25 | 15 | 5 | 25 | 15 | 5 | 25 | 15 | 5 | 25 | 15 | a
Energy installation cost | 5.25 | 100 | 21 | 5.25 | 100 | 21 | 5.25 | 100 | 21 | 5.25 | 100 | 21 | USD / kWh
Power installation cost | 525 | 2000 | 840 | 525 | 2000 | 840 | 525 | 2000 | 840 | 525 | 2000 | 840 | USD / kW

## CAES (calc) (hidden)
| CAES | [6 empty] | Sources
|  | 2016 | 2020 | 2025 | 2030 | unit |  | Source 2016 | Source 2020 | Source 2025 | Source 2030
| Energy installation cost | 52.5 | 48.096 | 45.7021 | 44.1848 | USD / kWh |  | 2016
| Power installation cost | 945 | 781.6273 | 712.6978 | 693.4096 | USD / kW |  | 2016 | 1 | 1 | 1
| Cycle life | 50000 | 50000 | 50000 | 50000 | equivalent full-cycles |  | 2016 | 2 | 2 | 2
| Calendar life | 50 | 50 | 50 | 50 | a |  | 2016
| Round-trip efficiency | 60 | 64 | 67 | 68 | % |  | 2016 | 2 | 2 | 2
interpolated
| References | [8 empty] | extrapolated
| Number of Source | Titel | Authors | Web | Date |  |  |  |  | not needed or not available
| 1 | Technology Overview on Electricity Storage | Fuchs, Lunz, Leuthold, Sauer | http://www.sefep.eu/activities/projects-studies/120628_Technology_Overview_Electricity_Storage_SEFEP_ISEA.pdf | June 2012
| 2 | Energiesysteme der Zukunft - Technologiesteckbrief Energiespeicher | Prof. Dr. Peter Elsner, Prof. Dr. Dirk Uwe Sauer | http://www.acatech.de/fileadmin/user_upload/Baumstruktur_nach_Website/Acatech/root/de/Publikationen/Materialien/ESYS_Technologiesteckbrief_Energiespeicher.pdf | November 2015
Percental
Interpolation |  | ref | source
Source 1 |  | 2016 | 2012 | 2020 | 2023 | 2025 | 2030 |  | unit | X1 | X2
| Energy installation cost | 50 | 60 | 60 |  | 60 | 60 |  | USD / kWh | 0
| Power installation cost | 900 | 1000 | 853.404 |  | 772.9054 | 700 |  | USD / kW | 0.01962
| Cycle life | 50000 | 9999999 | 9999999 |  | 9999999 | 9999999 |  | equivalent full-cycles | 0
| Calendar life | 50 | 25 | 25 |  | 25 | 25 |  | a | 0
| Round-trip efficiency | 60 | 65 | 65 |  | 65 | 65 |  | % | 0
Source 2 |  | 2016 | 2013 | 2020 | 2023 | 2025 | 2030 | 2050 | unit
| Energy installation cost | 50 | 34 | 31.1479 | 30 | 29.5976 | 28.6149 | 25 | USD / kWh | 0.012438 | 0.0067299
| Power installation cost | 900 | 1000 | 827.1188 | 762.5 | 754.1776 | 733.7668 | 657.5 | USD / kW | 0.026751 | 0.0054723
| Cycle life | 50000 | 100000 | 100000 | 100000 | 100000 | 100000 | 100000 | equivalent full-cycles | 0 | 0
| Calendar life | 50 | 25 | 28.4032 | 30 | 30.6462 | 32.3231 | 40 | a | -0.018399 | -0.010712
| Round-trip efficiency | 60 | 65 | 67.0857 | 68 | 68.2885 | 69.0152 | 72 | % | -0.0045222 | -0.0021192

## CAES (hidden)
| 2016 |  |  | 2020 |  |  | 2025 |  |  | 2030
CAES (calc) | best | worst | reference | best | worst | reference | best | worst | reference | best | worst | reference | unit
Energy density | 6 | 2 | 3 | 6 | 2 | 3 | 6 | 2 | 3 | 6 | 2 | 3 | Wh/l
Power density | 0.6 | 0.2 | 0.4 | 0.6 | 0.2 | 0.4 | 0.6 | 0.2 | 0.4 | 0.6 | 0.2 | 0.4 | W/l
Cycle life | 100000 | 10000 | 50000 | 100000 | 10000 | 50000 | 100000 | 10000 | 50000 | 100000 | 10000 | 50000 | equivalent full-cycles
Calendar life | 100 | 20 | 50 | 100 | 20 | 50 | 100 | 20 | 50 | 100 | 20 | 50 | a
Depth of discharge | 50 | 35 | 40 | 50 | 35 | 40 | 50 | 35 | 40 | 50 | 35 | 40 | %
Round-trip efficiency | 75 | 40 | 60 | 80 | 42.6667 | 64 | 83.75 | 44.6667 | 67 | 85 | 45.3333 | 68 | %
Self-discharge | 0 | 1 | 0.5 | 0 | 1 | 0.5 | 0 | 1 | 0.5 | 0 | 1 | 0.5 | % per day
Power dynamic | sec | 900 | 480 | 0 | 900 | 480 | 0 | 900 | 480 | 0 | 900 | 480 | s to rated power
Planning & Construction Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | a
Energy installation cost | 2 | 84 | 52.5 | 1.8322 | 76.9536 | 48.096 | 1.741 | 73.1234 | 45.7021 | 1.6832 | 70.6957 | 44.1848 | USD / kWh
Power installation cost | 400 | 1050 | 945 | 330.8475 | 868.4747 | 781.6273 | 301.671 | 791.8865 | 712.6978 | 293.5067 | 770.4551 | 693.4096 | USD / kW

## Flywheel (calc) (hidden)
Example | [5 empty] | Sources
| 2016 | 2020 | 2025 | 2030 | unit | Source 2016 | Source 2020 | Source 2025 | Source 2030
Energy installation cost | 3000 | 2655.8784 | 2280.6932 | 1958.5088 | USD / kWh | 1
Power installation cost | 300 | 265.5878 | 228.0693 | 195.8509 | USD / kW | 1
Cycle life | 200000 | 225101.762 | 260954.6368 | 302517.945 | equivalent full-cycles | 2016
Calendar life | 20 | 22.5102 | 26.0955 | 30.2518 | a | 2016
Round-trip efficiency | 84 | 85 | 86 | 87 | % | 2016
Note: As no reliable data could be found, a simple estimation of 3% annual performance increase / price decrease was used as a reference. For the round-trip efficiency, an increase of 1 percent point per period was assumed.
References
Number of Source | Titel | Authors | Internal File

## Flywheel (hidden)
| 2016 |  |  | 2020 |  |  | 2025 |  |  | 2030
Flywheel (calc) | best | worst | reference | best | worst | reference | best | worst | reference | best | worst | reference | unit
Energy density | 200 | 20 | 80 | 200 | 20 | 80 | 200 | 20 | 80 | 200 | 20 | 80 | Wh/l
Power density | 10000 | 5000 | 7500 | 10000 | 5000 | 7500 | 10000 | 5000 | 7500 | 10000 | 5000 | 7500 | W/l
Cycle life | 1000000 | 100000 | 200000 | 1125508.81 | 112550.881 | 225101.762 | 1304773.1838 | 130477.3184 | 260954.6368 | 1512589.7249 | 151258.9725 | 302517.945 | equivalent full-cycles
Calendar life | 25 | 15 | 20 | 28.1377 | 16.8826 | 22.5102 | 32.6193 | 19.5716 | 26.0955 | 37.8147 | 22.6888 | 30.2518 | a
Depth of discharge | 90 | 75 | 85 | 90 | 75 | 85 | 90 | 75 | 85 | 90 | 75 | 85 | %
Round-trip efficiency | 99 | 70 | 84 | 99 | 70.8333 | 85 | 99 | 71.6667 | 86 | 99 | 72.5 | 87 | %
Self-discharge | 20 | 100 | 60 | 15.6749 | 78.3743 | 53.1176 | 11.559 | 57.7951 | 45.6139 | 8.5239 | 42.6195 | 39.1702 | % per day
Power dynamic | < 0,004 | sec | 0.05 | 0 | 0 | 0.05 | 0 | 0 | 0.05 | 0 | 0 | 0.05 | s to rated power
Planning & Construction Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | a
Energy installation cost | 1500 | 6000 | 3000 | 1327.9392 | 5311.7569 | 2655.8784 | 1140.3466 | 4561.3864 | 2280.6932 | 979.2544 | 3917.0177 | 1958.5088 | USD / kWh
Power installation cost | 315 | 1050 | 300 | 278.8672 | 929.5575 | 265.5878 | 239.4728 | 798.2426 | 228.0693 | 205.6434 | 685.4781 | 195.8509 | USD / kW

## Flooded LA (calc) (hidden)
| Flooded LA | [8 empty] | Sources
|  | 2016 | 2020 | 2025 | 2030 | unit |  | Source 2016 | Source 2020 | Source 2025 | Source 2030 |  | 0.048031
| Energy installation cost | 147 | 120.7282 | 94.3893 | 73.7967 | USD / kWh |  | ref 2016 | Combination | Combination | Combination
| Power installation cost | 0 | 0 | 0 | 0 | USD / kW |  | ref 2016 | 1 | 1 | 1 |  | -0.056199
| Cycle life | 1500 | 1866.6963 | 2453.5883 | 3225 | equivalent full-cycles |  | ref 2016 | Combination | Combination | Combination |  | -0.025191
| Calendar life | 9 | 9.9417 | 11.2586 | 12.75 | a |  | ref 2016 | Combination | Combination | Combination |  | -0.0029767
| Round-trip efficiency | 82 | 82.9807 | 84.2232 | 85.4842 | % |  | ref 2016 | Combination | Combination | Combination
interpolated
| References | [8 empty] | extrapolated
| Number of Source | Titel | Authors | Web | Date |  | Type |  |  | not needed or not available
| 1 | Technology Overview on Electricity Storage | Fuchs, Lunz, Leuthold, Sauer | http://www.sefep.eu/activities/projects-studies/120628_Technology_Overview_Electricity_Storage_SEFEP_ISEA.pdf | June 2012 |  | lead-acid batteries
| 2 | Agora Stromspeicher in der Energiewende | Agora Energiewende | http://www.speicherinitiative.at/assets/Uploads/19-AgoraEnergiewende-Speicherstudie-Langfassung.pdf | September 2014 |  | lead-acid batteries
| 3 | Batteriespeicher in der Nieder- und Mittelspannungsebene | VDE | http://www.speicherinitiative.at/assets/Uploads/03-Batterienspeicher.pdf | Mai 2015 |  | lead-acid batteries
| 4 | Energiesysteme der Zukunft - Technologiesteckbrief Energiespeicher | Prof. Dr. Peter Elsner, Prof. Dr. Dirk Uwe Sauer | http://www.acatech.de/fileadmin/user_upload/Baumstruktur_nach_Website/Acatech/root/de/Publikationen/Materialien/ESYS_Technologiesteckbrief_Energiespeicher.pdf | November 2015 |  | lead-acid batteries
| 5 | Battery Storage for Renewables: Market Status and Technology Outlook | Ruud Kempener (IRENA) and Eric Borden | http://www.irena.org/documentdownloads/publications/irena_battery_storage_report_2015.pdf | January 2015 |  | advanced lead-acid
Percental
Interpolation |  | ref | source
Source 1 |  | 2016 | 2012 | 2020 | 2023 | 2025 | 2030 | 2033 | unit | X1 | X2 | S. 44
| Energy installation cost | 140 | 175 | 112.6864 |  | 85.584 | 65 |  | € / kWh | 0.053536
| Power installation cost | 0 | 175 | 100.2836 |  | 70.8109 | 50 |  | € / kW | 0.067231
| Cycle life | 1500 | 1250 | 1911.3605 |  | 2492.3727 | 3250 |  | equivalent full-cycles | -0.054518
| Calendar life | 9 | 10 | 11.9746 |  | 13.4022 | 15 |  | a | -0.022781
| Round-trip efficiency | 82 | 77.5 | 79.253 |  | 80.3686 | 81.5 |  | % | -0.0027997
Source 2 |  | 2016 | 2014 | 2020 | 2023 | 2025 | 2030 | 2033 | unit |  |  | S. 127-128
| Energy installation cost | 140 | 200 | 142.2757 | 120 | 115.7031 | 105.622 | 100 | € / kWh | 0.055178 | 0.018067 | S. 127-128
| Power installation cost | 0 | 160 | 109.0272 | 90 | 76.5255 | 51.017 | 40 | € / kW | 0.061929 | 0.077892 | S. 127-128
| Cycle life | 1500 | [6 empty] | equivalent full-cycles
| Calendar life | 9 | 8 | 9.2832 | 10 | 10 | 10 | 10 | a | -0.025104 | 0 | S. 127-128
| Round-trip efficiency | 82 | 80 | 80 | 80 | 80 | 80 | 80 | % | 0 | 0 | S. 127-128
Source 3 |  | 2016 | 2015 | 2020 | 2023 | 2025 | 2030 | 2033 | unit
| Energy installation cost | 140 | 175 | 117.5 |  | 90 |  |  | € / kWh |  |  | S. 93 | im Text: 235 €/kWH in 2014
| Power installation cost | 0 | 125 | 92.5 |  | 75 |  |  | € / kW |  |  | S. 95
| Cycle life | 1500 | 1250 | 2500 |  | 2850.4386 | 3250 |  | equivalent full-cycles |  | -0.026584 | S.64
| Calendar life | 9 | 10 | 12 |  | 13.4164 | 15 |  | a |  | -0.022565 | S.64
| Round-trip efficiency | 80 | 85 | 90 |  | 90 | 90 |  | % |  | 0 | S.64 | Batterie, auch daten für Bat plus Umrichter
Source 4 |  | 2016 | 2013 | 2020 | 2023 | 2025 | 2030 | 2033 | unit |  |  | technische Daten aus 2013! | 2050
| Energy installation cost | 140 |  |  | 136.5 |  |  |  | € / kWh | 0.0036103 |  | S. 23 | 120
| Power installation cost | 0 |  |  | 72.5 |  |  |  | € / kW |  |  | S. 23 | 45
| Cycle life | 1500 | 2500 | 2500 | 2500 | 2500 |  |  | equivalent full-cycles | 0 | 0 | S. 23 | 2500
| Calendar life | 9 | 10.5 | 9.8027 | 13 | 13.5425 |  |  | a | -0.021587 | -0.020653 | S. 23 | 15
| Round-trip efficiency | 82 | 84 | 83.1591 | 87 | 87.5668 | 89 |  | % | -0.0035153 | -0.0032522 | S. 23 | 89
Source 5 |  | 2016 | 2014 | 2017 | 2020 | 2025 | 2030 | 2050 | unit |  |  | Preise aus 2014! | 2013
| Energy installation cost | 147 | 600 | 550 | 500 | 426.562 | 363.9103 |  | USD / kWh | 0.028587 | 0.031271 | S.30
| Power installation cost | 0 | [6 empty] | USD / kW
| Cycle life | 1500 | [6 empty] | equivalent full-cycles |  |  | S. 41 | 2800
| Calendar life | 9 | [6 empty] | a |  |  | S. 41 | up to 17
| Round-trip efficiency | 82 | [6 empty] | %
|  |  | price | cycle life | calender | efficiency
|  |  | 37.14% | 260% | 150% | 105.2%
|  |  | 52.81% | 125% | 125% | 100%
|  |  | 60.65% | 260% | 150% | 105.9%
106%
|  |  | avg | avg | avg | avg
|  |  | 50.2% | 215% | 141.7% | 104.2%

## Flooded LA (hidden)
| 2016 |  |  | 2020 |  |  | 2025 |  |  | 2030
Flooded LA (calc) | best | worst | reference | best | worst | reference | best | worst | reference | best | worst | reference | unit
Energy density | 100 | 50 | 80 | 100 | 50 | 80 | 100 | 50 | 80 | 100 | 50 | 80 | Wh/l
Power density | 700 | 10 | 350 | 700 | 10 | 350 | 700 | 10 | 350 | 700 | 10 | 350 | W/l
Cycle life | 2500 | 250 | 1500 | 3111.1606 | 311.1161 | 1866.6963 | 4089.3139 | 408.9314 | 2453.5883 | 5375 | 537.5 | 3225 | equivalent full-cycles
Calendar life | 15 | 3 | 9 | 16.5695 | 3.3139 | 9.9417 | 18.7644 | 3.7529 | 11.2586 | 21.25 | 4.25 | 12.75 | a
Depth of discharge | 50 | 60 | 50 | 50 | 60 | 50 | 50 | 60 | 50 | 50 | 60 | 50 | %
Round-trip efficiency | 92 | 75 | 82 | 93.1003 | 75.897 | 82.9807 | 94.4943 | 77.0334 | 84.2232 | 95.9091 | 78.1868 | 85.4842 | %
Self-discharge | 0.09 | 0.4 | 0.25 | 0.09 | 0.4 | 0.25 | 0.09 | 0.4 | 0.25 | 0.09 | 0.4 | 0.25 | % per day
Power dynamic | 0.003 | 0.01 | 0.006 | 0.003 | 0.01 | 0.006 | 0.003 | 0.01 | 0.006 | 0.003 | 0.01 | 0.006 | s to rated power
Planning & Construction Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | a
Energy installation cost | 105 | 472.5 | 147 | 86.2344 | 388.0549 | 120.7282 | 67.421 | 303.3943 | 94.3893 | 52.712 | 237.2038 | 73.7967 | USD / kWh
Power installation cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | USD / kW

## VRLA (calc) (hidden)
| LA | [8 empty] | Sources
|  | 2016 | 2020 | 2025 | 2030 | unit |  | Source 2016 | Source 2020 | Source 2025 | Source 2030 |  | 0.048031
| Energy installation cost | 262.5 | 215.5861 | 168.5524 | 131.7799 | USD / kWh |  | ref 2016 | Combination | Combination | Combination
| Power installation cost | 0 | 0 | 0 | 0 | USD / kW |  | ref 2016 | 1 | 1 | 1 |  | -0.056199
| Cycle life | 1500 | 1866.6963 | 2453.5883 | 3225 | equivalent full-cycles |  | ref 2016 | Combination | Combination | Combination |  | -0.025191
| Calendar life | 9 | 9.9417 | 11.2586 | 12.75 | a |  | ref 2016 | Combination | Combination | Combination |  | -0.0029767
| Round-trip efficiency | 80 | 80.9568 | 82.1689 | 83.3992 | % |  | ref 2016 | Combination | Combination | Combination
interpolated
| References | [8 empty] | extrapolated
| Number of Source | Titel | Authors | Web | Date |  | Type |  |  | not needed or not available
| 1 | Technology Overview on Electricity Storage | Fuchs, Lunz, Leuthold, Sauer | http://www.sefep.eu/activities/projects-studies/120628_Technology_Overview_Electricity_Storage_SEFEP_ISEA.pdf | June 2012 |  | lead-acid batteries
| 2 | Agora Stromspeicher in der Energiewende | Agora Energiewende | http://www.speicherinitiative.at/assets/Uploads/19-AgoraEnergiewende-Speicherstudie-Langfassung.pdf | September 2014 |  | lead-acid batteries
| 3 | Batteriespeicher in der Nieder- und Mittelspannungsebene | VDE | http://www.speicherinitiative.at/assets/Uploads/03-Batterienspeicher.pdf | Mai 2015 |  | lead-acid batteries
| 4 | Energiesysteme der Zukunft - Technologiesteckbrief Energiespeicher | Prof. Dr. Peter Elsner, Prof. Dr. Dirk Uwe Sauer | http://www.acatech.de/fileadmin/user_upload/Baumstruktur_nach_Website/Acatech/root/de/Publikationen/Materialien/ESYS_Technologiesteckbrief_Energiespeicher.pdf | November 2015 |  | lead-acid batteries
| 5 | Battery Storage for Renewables: Market Status and Technology Outlook | Ruud Kempener (IRENA) and Eric Borden | http://www.irena.org/documentdownloads/publications/irena_battery_storage_report_2015.pdf | January 2015 |  | advanced lead-acid
Percental
Interpolation |  | ref | source
Source 1 |  | 2016 | 2012 | 2020 | 2023 | 2025 | 2030 | 2033 | unit | X1 | X2 | S. 44
| Energy installation cost | 250 | 175 | 112.6864 |  | 85.584 | 65 |  | € / kWh | 0.053536
| Power installation cost | 0 | 175 | 100.2836 |  | 70.8109 | 50 |  | € / kW | 0.067231
| Cycle life | 1500 | 1250 | 1911.3605 |  | 2492.3727 | 3250 |  | equivalent full-cycles | -0.054518
| Calendar life | 9 | 10 | 11.9746 |  | 13.4022 | 15 |  | a | -0.022781
| Round-trip efficiency | 80 | 77.5 | 79.253 |  | 80.3686 | 81.5 |  | % | -0.0027997
Source 2 |  | 2016 | 2014 | 2020 | 2023 | 2025 | 2030 | 2033 | unit |  |  | S. 127-128
| Energy installation cost | 250 | 200 | 142.2757 | 120 | 115.7031 | 105.622 | 100 | € / kWh | 0.055178 | 0.018067 | S. 127-128
| Power installation cost | 0 | 160 | 109.0272 | 90 | 76.5255 | 51.017 | 40 | € / kW | 0.061929 | 0.077892 | S. 127-128
| Cycle life | 1500 | [6 empty] | equivalent full-cycles
| Calendar life | 9 | 8 | 9.2832 | 10 | 10 | 10 | 10 | a | -0.025104 | 0 | S. 127-128
| Round-trip efficiency | 80 | 80 | 80 | 80 | 80 | 80 | 80 | % | 0 | 0 | S. 127-128
Source 3 |  | 2016 | 2015 | 2020 | 2023 | 2025 | 2030 | 2033 | unit
| Energy installation cost | 250 | 175 | 117.5 |  | 90 |  |  | € / kWh |  |  | S. 93 | im Text: 235 €/kWH in 2014
| Power installation cost | 0 | 125 | 92.5 |  | 75 |  |  | € / kW |  |  | S. 95
| Cycle life | 1500 | 1250 | 2500 |  | 2850.4386 | 3250 |  | equivalent full-cycles |  | -0.026584 | S.64
| Calendar life | 9 | 10 | 12 |  | 13.4164 | 15 |  | a |  | -0.022565 | S.64
| Round-trip efficiency | 80 | 85 | 90 |  | 90 | 90 |  | % |  | 0 | S.64 | Batterie, auch daten für Bat plus Umrichter
Source 4 |  | 2016 | 2013 | 2020 | 2023 | 2025 | 2030 | 2033 | unit |  |  | technische Daten aus 2013! | 2050
| Energy installation cost | 250 |  |  | 136.5 |  |  |  | € / kWh | 0.082817 |  | S. 23 | 120
| Power installation cost | 0 |  |  | 72.5 |  |  |  | € / kW |  |  | S. 23 | 45
| Cycle life | 1500 | 2500 | 2500 | 2500 | 2500 |  |  | equivalent full-cycles | 0 | 0 | S. 23 | 2500
| Calendar life | 9 | 10.5 | 9.8027 | 13 | 13.5425 |  |  | a | -0.021587 | -0.020653 | S. 23 | 15
| Round-trip efficiency | 80 | 84 | 81.1308 | 87 | 87.5668 | 89 |  | % | -0.0035153 | -0.0032522 | S. 23 | 89
Source 5 |  | 2016 | 2014 | 2017 | 2020 | 2025 | 2030 | 2050 | unit |  |  | Preise aus 2014! | 2013
| Energy installation cost | 262.5 | 600 | 550 | 500 | 426.562 | 363.9103 |  | USD / kWh | 0.028587 | 0.031271 | S.30
| Power installation cost | 0 | [6 empty] | USD / kW
| Cycle life | 1500 | [6 empty] | equivalent full-cycles |  |  | S. 41 | 2800
| Calendar life | 9 | [6 empty] | a |  |  | S. 41 | up to 17
| Round-trip efficiency | 80 | [6 empty] | %
|  |  | price | cycle life | calender | efficiency
|  |  | 37.14% | 260% | 150% | 105.2%
|  |  | 52.81% | 125% | 125% | 100%
|  |  | 60.65% | 260% | 150% | 105.9%
106%
|  |  | avg | avg | avg | avg
|  |  | 50.2% | 215% | 141.7% | 104.2%

## VRLA (hidden)
| 2016 |  |  | 2020 |  |  | 2025 |  |  | 2030
VRLA (calc) | best | worst | reference | best | worst | reference | best | worst | reference | best | worst | reference | unit
Energy density | 100 | 50 | 80 | 100 | 50 | 80 | 100 | 50 | 80 | 100 | 50 | 80 | Wh/l
Power density | 700 | 10 | 350 | 700 | 10 | 350 | 700 | 10 | 350 | 700 | 10 | 350 | W/l
Cycle life | 2500 | 250 | 1500 | 3111.1606 | 311.1161 | 1866.6963 | 4089.3139 | 408.9314 | 2453.5883 | 5375 | 537.5 | 3225 | equivalent full-cycles
Calendar life | 15 | 3 | 9 | 16.5695 | 3.3139 | 9.9417 | 18.7644 | 3.7529 | 11.2586 | 21.25 | 4.25 | 12.75 | a
Depth of discharge | 50 | 60 | 50 | 50 | 60 | 50 | 50 | 60 | 50 | 50 | 60 | 50 | %
Round-trip efficiency | 92 | 75 | 80 | 93.1003 | 75.897 | 80.9568 | 94.4943 | 77.0334 | 82.1689 | 95.9091 | 78.1868 | 83.3992 | %
Self-discharge | 0.09 | 0.4 | 0.25 | 0.09 | 0.4 | 0.25 | 0.09 | 0.4 | 0.25 | 0.09 | 0.4 | 0.25 | % per day
Power dynamic | 0.003 | 0.01 | 0.006 | 0.003 | 0.01 | 0.006 | 0.003 | 0.01 | 0.006 | 0.003 | 0.01 | 0.006 | s to rated power
Planning & Construction Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | a
Energy installation cost | 105 | 472.5 | 262.5 | 86.2344 | 388.0549 | 215.5861 | 67.421 | 303.3943 | 168.5524 | 52.712 | 237.2038 | 131.7799 | USD / kWh
Power installation cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | USD / kW

## Li-Ion (NMC) (calc) (hidden)
| Li-Ion (NMC) | [8 empty] | Sources
|  | 2016 | 2020 | 2025 | 2030 | unit |  | Source 2016 | Source 2020 | Source 2025 | Source 2030 |  | 0.063625
| Energy installation cost | 420 | 322.886 | 232.4338 | 167.3205 | USD / kWh |  | ref 2016 | combination | combination | combination
| Power installation cost | 0 | 0 | 0 | 0 | USD / kW |  | ref 2016 | 1 | 1 | 1 |  | -0.047295
| Cycle life | 2000 | 2406.0581 | 3031.456 | 3819.4112 | equivalent full-cycles |  | ref 2016 | combination | combination | combination |  | -0.030926
| Calendar life | 12 | 13.5547 | 15.7844 | 18.3809 | a |  | ref 2016 | combination | combination | combination |  | -0.0013078
| Round-trip efficiency | 95 | 95.4979 | 96.1241 | 96.7543 | % |  | ref 2016 | combination | combination | combination
interpolated
| References | [8 empty] | extrapolated
| Number of Source | Titel | Authors | Web | Date |  | Type |  |  | not needed or not available
| 1 | Technology Overview on Electricity Storage | Fuchs, Lunz, Leuthold, Sauer | http://www.sefep.eu/activities/projects-studies/120628_Technology_Overview_Electricity_Storage_SEFEP_ISEA.pdf | June 2012 |  | lithium-ion batteries
| 2 | Agora Stromspeicher in der Energiewende | Agora Energiewende | http://www.speicherinitiative.at/assets/Uploads/19-AgoraEnergiewende-Speicherstudie-Langfassung.pdf | September 2014 |  | lithium-ion batteries
| 3 | Batteriespeicher in der Nieder- und Mittelspannungsebene | VDE | http://www.speicherinitiative.at/assets/Uploads/03-Batterienspeicher.pdf | Mai 2015 |  | lithium-ion batteries
| 4 | Energiesysteme der Zukunft - Technologiesteckbrief Energiespeicher | Prof. Dr. Peter Elsner, Prof. Dr. Dirk Uwe Sauer | http://www.acatech.de/fileadmin/user_upload/Baumstruktur_nach_Website/Acatech/root/de/Publikationen/Materialien/ESYS_Technologiesteckbrief_Energiespeicher.pdf | November 2015 |  | lithium-ion batteries
| 5 | Battery Storage for Renewables: Market Status and Technology Outlook | Ruud Kempener (IRENA) and Eric Borden | http://www.irena.org/documentdownloads/publications/irena_battery_storage_report_2015.pdf | January 2015 |  | NMC
Percental
Interpolation |  | ref | source
Source 1 |  | 2016 | 2012 | 2020 | 2023 | 2025 | 2030 | 2033 | unit | X1 | X2 | Seite | Kommentar
| Energy installation cost | 400 | 550 | 369.6904 |  | 288.41 | 225 |  | € / kWh | 0.048444 |  | S.42
| Power installation cost | 0 | 175 | 100.2836 |  | 70.8109 | 50 |  | € / kW | 0.067231 |  | S.42
| Cycle life | 2000 | 3000 | 4230.2125 |  | 5243.6992 | 6500 |  | equivalent full-cycles | -0.043891 |  | S.42
| Calendar life | 12 | 12.5 | 15.4039 |  | 17.5521 | 20 |  | a | -0.026455 |  | S.42
| Round-trip efficiency | 95 | 84.5 | 86.255 |  | 87.3703 | 88.5 |  | % | -0.0025728 |  | S.42
Source 2 |  | 2016 | 2014 | 2020 | 2023 | 2025 | 2030 | 2033 | unit |  |  | S. 127-128
| Energy installation cost | 400 | 550 | 406.9112 | 350 | 333.5193 | 295.6333 | 275 | € / kWh | 0.04898 | 0.023828 | S. 127-128
| Power installation cost | 0 | 160 |  | 90 |  |  | 40 | € / kW |  |  | S. 127-128
| Cycle life | 2000 | [6 empty] | equivalent full-cycles
| Calendar life | 12 | 12 | 13.9248 | 15 | 15.8884 | 18.3463 | 20 | a | -0.025104 | -0.029186 | S. 127-128
| Round-trip efficiency | 95 | 90 | 90 | 90 | 90 | 90 | 90 | % | 0 | 0 | S. 127-128
Source 3 |  | 2016 | 2015 | 2020 | 2023 | 2025 | 2030 | 2033 | unit
| Energy installation cost | 400 | 285 | 180 |  | 145 | 116.8056 |  | € / kWh | 0.057732 | 0.042323 | S. 90 | Es gibt auch Preise von Li-Ionen-System PV Speicher (2015: 750€/kWh - 1250€/kWh 2020
| Power installation cost | 0 | 125 | 92.5 |  | 75 |  |  | € / kW |  |  | S. 95
| Cycle life | 2000 | 3000 | 5000 |  | 5916.0798 | 7000 |  | equivalent full-cycles | -0.058112 | -0.03422 | S. 61
| Calendar life | 12 | 12.5 | 20 |  | 20 | 20 |  | a | -0.03183 | 0 | S. 61
| Round-trip efficiency | 95 | 97 | 97 |  | 97 | 97 |  | % | 0 | 0 | S. 61
Source 4 |  | 2016 | 2013 | 2020 | 2023 | 2025 | 2030 | 2050 | unit
| Energy installation cost | 400 | 445 | 199.0496 | 141 | 138.0029 | 130.786 | 105.5 | € / kWh | 0.10857 | 0.010685 | S. 31-32 | Kosten sind für Großspeicher eingetragen, es gibt aber auch PV
| Power installation cost | 0 | 160 |  | 72.5 |  |  | 45 | € / kW |  |  | S. 31-32
| Cycle life | 2000 | 5000 | 6327.9003 | 7000 | 7285.1339 | 8049.822 | 12000 | equivalent full-cycles | -0.03422 | -0.020163 | S. 31-32
| Calendar life | 12 | 13 | 15.6855 | 17 | 17.3278 | 18.1752 | 22 | a | -0.027189 | -0.009595 | S. 31-32
| Round-trip efficiency | 95 | 85.5 | 86.5473 | 87 | 87.2188 | 87.768 | 90 | % | -0.0017407 | -0.0012564 | S. 31-32 | Sehr gering!
Source 5 |  | 2016 | 2014 | 2017 | 2020 | 2025 | 2030 | 2050 | unit
| Energy installation cost | 420 | 600 | 500 | 300 | 128.0482 | 54.6544 |  | USD / kWh | 0.058964 | 0.15657 | S- 30
| Power installation cost | 0 | [6 empty] | USD / kW
| Cycle life | 2000 | [6 empty] | equivalent full-cycles
| Calendar life | 12 | [6 empty] | a
| Round-trip efficiency | 95 | [6 empty] | %
|  |  | price | cycle life | calender | efficiency
|  |  | 40.91% | 216.7% | 160% | 104.7%
|  |  | 53.75% | 152.9% | 152.9% | 100%
|  |  | 40.98% | 233.3% | 160% | 100%
|  |  | 23.71% | 161% | 139.8% | 102.7%
9.109%
|  |  | avg | avg | avg | avg
|  |  | 39.84% | 191% | 153.2% | 101.8%

## Li-Ion (NMC) (hidden)
| 2016 |  |  | 2020 |  |  | 2025 |  |  | 2030
Li-Ion (NMC) (calc) | best | worst | reference | best | worst | reference | best | worst | reference | best | worst | reference | unit
Energy density | 735 | 200 | 468 | 735 | 200 | 468 | 735 | 200 | 468 | 735 | 200 | 468 | Wh/l
Power density | 10000 | 100 | 3500 | 10000 | 100 | 3500 | 10000 | 100 | 3500 | 10000 | 100 | 3500 | W/l
Cycle life | 4000 | 500 | 2000 | 4812.1163 | 601.5145 | 2406.0581 | 6062.9119 | 757.864 | 3031.456 | 7638.8223 | 954.8528 | 3819.4112 | equivalent full-cycles
Calendar life | 20 | 5 | 12 | 22.5912 | 5.6478 | 13.5547 | 26.3073 | 6.5768 | 15.7844 | 30.6348 | 7.6587 | 18.3809 | a
Depth of discharge | 100 | 84 | 90 | 100 | 84 | 90 | 100 | 84 | 90 | 100 | 84 | 90 | %
Round-trip efficiency | 98 | 81 | 95 | 99 | 81.4246 | 95.4979 | 99 | 81.9584 | 96.1241 | 99 | 82.4957 | 96.7543 | %
Self-discharge | 0.09 | 0.36 | 0.1 | 0.09 | 0.36 | 0.1 | 0.09 | 0.36 | 0.1 | 0.09 | 0.36 | 0.1 | % per day
Power dynamic | 0.003 | 1 | 0.01 | 0.003 | 1 | 0.01 | 0.003 | 1 | 0.01 | 0.003 | 1 | 0.01 | s to rated power
Planning & Construction Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | a
Energy installation cost | 199.5 | 840 | 420 | 153.3709 | 645.7721 | 322.886 | 110.406 | 464.8675 | 232.4338 | 79.4772 | 334.641 | 167.3205 | USD / kWh
Power installation cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | USD / kW

## Li-Ion (NCA) (calc) (hidden)
| Li-Ion (NCA) | [8 empty] | Sources
|  | 2016 | 2020 | 2025 | 2030 | unit |  | Source 2016 | Source 2020 | Source 2025 | Source 2030 |  | 0.061278
| Energy installation cost | 351.75 | 273.1377 | 199.0976 | 145.1277 | USD / kWh |  | ref 2016 | combination | combination | combination
| Power installation cost | 0 | 0 | 0 | 0 | USD / kW |  | ref 2016 | 1 | 1 | 1 |  | -0.047295
| Cycle life | 1000 | 1203.0291 | 1515.728 | 1909.7056 | equivalent full-cycles |  | ref 2016 | combination | combination | combination |  | -0.030926
| Calendar life | 12 | 13.5547 | 15.7844 | 18.3809 | a |  | ref 2016 | combination | combination | combination |  | -0.0013078
| Round-trip efficiency | 95 | 95.4979 | 96.1241 | 96.7543 | % |  | ref 2016 | combination | combination | combination
interpolated
| References | [8 empty] | extrapolated
| Number of Source | Titel | Authors | Web | Date |  | Type |  |  | not needed or not available
| 1 | Technology Overview on Electricity Storage | Fuchs, Lunz, Leuthold, Sauer | http://www.sefep.eu/activities/projects-studies/120628_Technology_Overview_Electricity_Storage_SEFEP_ISEA.pdf | June 2012 |  | lithium-ion batteries
| 2 | Agora Stromspeicher in der Energiewende | Agora Energiewende | http://www.speicherinitiative.at/assets/Uploads/19-AgoraEnergiewende-Speicherstudie-Langfassung.pdf | September 2014 |  | lithium-ion batteries
| 3 | Batteriespeicher in der Nieder- und Mittelspannungsebene | VDE | http://www.speicherinitiative.at/assets/Uploads/03-Batterienspeicher.pdf | Mai 2015 |  | lithium-ion batteries
| 4 | Energiesysteme der Zukunft - Technologiesteckbrief Energiespeicher | Prof. Dr. Peter Elsner, Prof. Dr. Dirk Uwe Sauer | http://www.acatech.de/fileadmin/user_upload/Baumstruktur_nach_Website/Acatech/root/de/Publikationen/Materialien/ESYS_Technologiesteckbrief_Energiespeicher.pdf | November 2015 |  | lithium-ion batteries
| 5 | Battery Storage for Renewables: Market Status and Technology Outlook | Ruud Kempener (IRENA) and Eric Borden | http://www.irena.org/documentdownloads/publications/irena_battery_storage_report_2015.pdf | January 2015 |  | NCA
Percental
Interpolation |  | ref | source
Source 1 |  | 2016 | 2012 | 2020 | 2023 | 2025 | 2030 | 2033 | unit | X1 | X2 | Seite | Kommentar
| Energy installation cost | 335 | 550 | 369.6904 |  | 288.41 | 225 |  | € / kWh | 0.048444 |  | S.42
| Power installation cost | 0 | 175 | 100.2836 |  | 70.8109 | 50 |  | € / kW | 0.067231 |  | S.42
| Cycle life | 1000 | 3000 | 4230.2125 |  | 5243.6992 | 6500 |  | equivalent full-cycles | -0.043891 |  | S.42
| Calendar life | 12 | 12.5 | 15.4039 |  | 17.5521 | 20 |  | a | -0.026455 |  | S.42
| Round-trip efficiency | 95 | 84.5 | 86.255 |  | 87.3703 | 88.5 |  | % | -0.0025728 |  | S.42
Source 2 |  | 2016 | 2014 | 2020 | 2023 | 2025 | 2030 | 2033 | unit |  |  | S. 127-128
| Energy installation cost | 335 | 550 | 406.9112 | 350 | 333.5193 | 295.6333 | 275 | € / kWh | 0.04898 | 0.023828 | S. 127-128
| Power installation cost | 0 | 160 |  | 90 |  |  | 40 | € / kW |  |  | S. 127-128
| Cycle life | 1000 | [6 empty] | equivalent full-cycles
| Calendar life | 12 | 12 | 13.9248 | 15 | 15.8884 | 18.3463 | 20 | a | -0.025104 | -0.029186 | S. 127-128
| Round-trip efficiency | 95 | 90 | 90 | 90 | 90 | 90 | 90 | % | 0 | 0 | S. 127-128
Source 3 |  | 2016 | 2015 | 2020 | 2023 | 2025 | 2030 | 2033 | unit
| Energy installation cost | 335 | 285 | 180 |  | 145 | 116.8056 |  | € / kWh | 0.057732 | 0.042323 | S. 90 | Es gibt auch Preise von Li-Ionen-System PV Speicher (2015: 750€/kWh - 1250€/kWh 2020
| Power installation cost | 0 | 125 | 92.5 |  | 75 |  |  | € / kW |  |  | S. 95
| Cycle life | 1000 | 3000 | 5000 |  | 5916.0798 | 7000 |  | equivalent full-cycles | -0.058112 | -0.03422 | S. 61
| Calendar life | 12 | 12.5 | 20 |  | 20 | 20 |  | a | -0.03183 | 0 | S. 61
| Round-trip efficiency | 95 | 97 | 97 |  | 97 | 97 |  | % | 0 | 0 | S. 61
Source 4 |  | 2016 | 2013 | 2020 | 2023 | 2025 | 2030 | 2050 | unit
| Energy installation cost | 335 | 445 | 199.0496 | 141 | 138.0029 | 130.786 | 105.5 | € / kWh | 0.10857 | 0.010685 | S. 31-32 | Kosten sind für Großspeicher eingetragen, es gibt aber auch PV
| Power installation cost | 0 | 160 |  | 72.5 |  |  | 45 | € / kW |  |  | S. 31-32
| Cycle life | 1000 | 5000 | 6327.9003 | 7000 | 7285.1339 | 8049.822 | 12000 | equivalent full-cycles | -0.03422 | -0.020163 | S. 31-32
| Calendar life | 12 | 13 | 15.6855 | 17 | 17.3278 | 18.1752 | 22 | a | -0.027189 | -0.009595 | S. 31-32
| Round-trip efficiency | 95 | 85.5 | 86.5473 | 87 | 87.2188 | 87.768 | 90 | % | -0.0017407 | -0.0012564 | S. 31-32 | Sehr gering!
Source 5 |  | 2016 | 2014 | 2017 | 2020 | 2025 | 2030 | 2050 | unit
| Energy installation cost | 351.75 | 320 | 280 | 180 | 86.1913 | 41.2719 |  | USD / kWh | 0.043534 | 0.13695 | S- 30
| Power installation cost | 0 | [6 empty] | USD / kW
| Cycle life | 1000 | [6 empty] | equivalent full-cycles
| Calendar life | 12 | [6 empty] | a
| Round-trip efficiency | 95 | [6 empty] | %
|  |  | price | cycle life | calender | efficiency
|  |  | 40.91% | 216.7% | 160% | 104.7%
|  |  | 53.75% | 152.9% | 152.9% | 100%
|  |  | 40.98% | 233.3% | 160% | 100%
|  |  | 29.39% | 161% | 139.8% | 102.7%
12.9%
|  |  | avg | avg | avg | avg
|  |  | 41.26% | 191% | 153.2% | 101.8%

## Li-Ion (NCA) (hidden)
| 2016 |  |  | 2020 |  |  | 2025 |  |  | 2030
Li-Ion (NCA) (calc) | best | worst | reference | best | worst | reference | best | worst | reference | best | worst | reference | unit
Energy density | 620 | 200 | 350 | 620 | 200 | 350 | 620 | 200 | 350 | 620 | 200 | 350 | Wh/l
Power density | 10000 | 100 | 3500 | 10000 | 100 | 3500 | 10000 | 100 | 3500 | 10000 | 100 | 3500 | W/l
Cycle life | 2000 | 500 | 1000 | 2406.0581 | 601.5145 | 1203.0291 | 3031.456 | 757.864 | 1515.728 | 3819.4112 | 954.8528 | 1909.7056 | equivalent full-cycles
Calendar life | 20 | 5 | 12 | 22.5912 | 5.6478 | 13.5547 | 26.3073 | 6.5768 | 15.7844 | 30.6348 | 7.6587 | 18.3809 | a
Depth of discharge | 100 | 84 | 90 | 100 | 84 | 90 | 100 | 84 | 90 | 100 | 84 | 90 | %
Round-trip efficiency | 98 | 81 | 95 | 98.5137 | 81.4246 | 95.4979 | 99 | 81.9584 | 96.1241 | 99 | 82.4957 | 96.7543 | %
Self-discharge | 0.09 | 0.36 | 0.2 | 0.09 | 0.36 | 0.2 | 0.09 | 0.36 | 0.2 | 0.09 | 0.36 | 0.2 | % per day
Power dynamic | 0.003 | 1 | 0.01 | 0.003 | 1 | 0.01 | 0.003 | 1 | 0.01 | 0.003 | 1 | 0.01 | s to rated power
Planning & Construction Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | a
Energy installation cost | 199.5 | 840 | 351.75 | 154.9139 | 652.2691 | 273.1377 | 112.921 | 475.457 | 199.0976 | 82.3113 | 346.5737 | 145.1277 | USD / kWh
Power installation cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | USD / kW

## Li-Ion (LFP) (calc) (hidden)
| Li-Ion (LFP) | [8 empty] | Sources
|  | 2016 | 2020 | 2025 | 2030 | unit |  | Source 2016 | Source 2020 | Source 2025 | Source 2030 |  | 0.06538
| Energy installation cost | 577.5 | 440.6489 | 314.2452 | 224.1014 | USD / kWh |  | ref 2016 | combination | combination | combination
| Power installation cost | 0 | 0 | 0 | 0 | USD / kW |  | ref 2016 | 1 | 1 | 1 |  | -0.047295
| Cycle life | 2500 | 3007.5727 | 3789.32 | 4774.264 | equivalent full-cycles |  | ref 2016 | combination | combination | combination |  | -0.030926
| Calendar life | 12 | 13.5547 | 15.7844 | 18.3809 | a |  | ref 2016 | combination | combination | combination |  | -0.0013078
| Round-trip efficiency | 92 | 92.4822 | 93.0886 | 93.6989 | % |  | ref 2016 | combination | combination | combination
interpolated
| References | [8 empty] | extrapolated
| Number of Source | Titel | Authors | Web | Date |  | Type |  |  | not needed or not available
| 1 | Technology Overview on Electricity Storage | Fuchs, Lunz, Leuthold, Sauer | http://www.sefep.eu/activities/projects-studies/120628_Technology_Overview_Electricity_Storage_SEFEP_ISEA.pdf | June 2012 |  | lithium-ion batteries
| 2 | Agora Stromspeicher in der Energiewende | Agora Energiewende | http://www.speicherinitiative.at/assets/Uploads/19-AgoraEnergiewende-Speicherstudie-Langfassung.pdf | September 2014 |  | lithium-ion batteries
| 3 | Batteriespeicher in der Nieder- und Mittelspannungsebene | VDE | http://www.speicherinitiative.at/assets/Uploads/03-Batterienspeicher.pdf | Mai 2015 |  | lithium-ion batteries
| 4 | Energiesysteme der Zukunft - Technologiesteckbrief Energiespeicher | Prof. Dr. Peter Elsner, Prof. Dr. Dirk Uwe Sauer | http://www.acatech.de/fileadmin/user_upload/Baumstruktur_nach_Website/Acatech/root/de/Publikationen/Materialien/ESYS_Technologiesteckbrief_Energiespeicher.pdf | November 2015 |  | lithium-ion batteries
| 5 | Battery Storage for Renewables: Market Status and Technology Outlook | Ruud Kempener (IRENA) and Eric Borden | http://www.irena.org/documentdownloads/publications/irena_battery_storage_report_2015.pdf | January 2015 |  | LFP
Percental
Interpolation |  | ref | source
Source 1 |  | 2016 | 2012 | 2020 | 2023 | 2025 | 2030 | 2033 | unit | X1 | X2 | Seite | Kommentar
| Energy installation cost | 550 | 550 | 369.6904 |  | 288.41 | 225 |  | € / kWh | 0.048444 |  | S.42
| Power installation cost | 0 | 175 | 100.2836 |  | 70.8109 | 50 |  | € / kW | 0.067231 |  | S.42
| Cycle life | 2500 | 3000 | 4230.2125 |  | 5243.6992 | 6500 |  | equivalent full-cycles | -0.043891 |  | S.42
| Calendar life | 12 | 12.5 | 15.4039 |  | 17.5521 | 20 |  | a | -0.026455 |  | S.42
| Round-trip efficiency | 92 | 84.5 | 86.255 |  | 87.3703 | 88.5 |  | % | -0.0025728 |  | S.42
Source 2 |  | 2016 | 2014 | 2020 | 2023 | 2025 | 2030 | 2033 | unit |  |  | S. 127-128
| Energy installation cost | 550 | 550 | 406.9112 | 350 | 333.5193 | 295.6333 | 275 | € / kWh | 0.04898 | 0.023828 | S. 127-128
| Power installation cost | 0 | 160 |  | 90 |  |  | 40 | € / kW |  |  | S. 127-128
| Cycle life | 2500 | [6 empty] | equivalent full-cycles
| Calendar life | 12 | 12 | 13.9248 | 15 | 15.8884 | 18.3463 | 20 | a | -0.025104 | -0.029186 | S. 127-128
| Round-trip efficiency | 92 | 90 | 90 | 90 | 90 | 90 | 90 | % | 0 | 0 | S. 127-128
Source 3 |  | 2016 | 2015 | 2020 | 2023 | 2025 | 2030 | 2033 | unit
| Energy installation cost | 550 | 285 | 180 |  | 145 | 116.8056 |  | € / kWh | 0.057732 | 0.042323 | S. 90 | Es gibt auch Preise von Li-Ionen-System PV Speicher (2015: 750€/kWh - 1250€/kWh 2020
| Power installation cost | 0 | 125 | 92.5 |  | 75 |  |  | € / kW |  |  | S. 95
| Cycle life | 2500 | 3000 | 5000 |  | 5916.0798 | 7000 |  | equivalent full-cycles | -0.058112 | -0.03422 | S. 61
| Calendar life | 12 | 12.5 | 20 |  | 20 | 20 |  | a | -0.03183 | 0 | S. 61
| Round-trip efficiency | 92 | 97 | 97 |  | 97 | 97 |  | % | 0 | 0 | S. 61
Source 4 |  | 2016 | 2013 | 2020 | 2023 | 2025 | 2030 | 2050 | unit
| Energy installation cost | 550 | 445 | 199.0496 | 141 | 138.0029 | 130.786 | 105.5 | € / kWh | 0.10857 | 0.010685 | S. 31-32 | Kosten sind für Großspeicher eingetragen, es gibt aber auch PV
| Power installation cost | 0 | 160 |  | 72.5 |  |  | 45 | € / kW |  |  | S. 31-32
| Cycle life | 2500 | 5000 | 6327.9003 | 7000 | 7285.1339 | 8049.822 | 12000 | equivalent full-cycles | -0.03422 | -0.020163 | S. 31-32
| Calendar life | 12 | 13 | 15.6855 | 17 | 17.3278 | 18.1752 | 22 | a | -0.027189 | -0.009595 | S. 31-32
| Round-trip efficiency | 92 | 85.5 | 86.5473 | 87 | 87.2188 | 87.768 | 90 | % | -0.0017407 | -0.0012564 | S. 31-32 | Sehr gering!
Source 5 |  | 2016 | 2014 | 2017 | 2020 | 2025 | 2030 | 2050 | unit
| Energy installation cost | 577.5 | 700 | 430 | 440 | 298.8236 | 202.9444 |  | USD / kWh | 0.14993 | 0.074466 | S- 30
| Power installation cost | 0 | [6 empty] | USD / kW
| Cycle life | 2500 | [6 empty] | equivalent full-cycles
| Calendar life | 12 | [6 empty] | a
| Round-trip efficiency | 92 | [6 empty] | %
|  |  | price | cycle life | calender | efficiency
|  |  | 40.91% | 216.7% | 160% | 104.7%
|  |  | 53.75% | 152.9% | 152.9% | 100%
|  |  | 40.98% | 233.3% | 160% | 100%
|  |  | 29.39% | 161% | 139.8% | 102.7%
28.99%
|  |  | avg | avg | avg | avg
|  |  | 38.81% | 191% | 153.2% | 101.8%

## Li-Ion (LFP) (hidden)
| 2016 |  |  | 2020 |  |  | 2025 |  |  | 2030
Li-Ion (LFP) (calc) | best | worst | reference | best | worst | reference | best | worst | reference | best | worst | reference | unit
Energy density | 620 | 200 | 350 | 620 | 200 | 350 | 620 | 200 | 350 | 620 | 200 | 350 | Wh/l
Power density | 10000 | 100 | 3500 | 10000 | 100 | 3500 | 10000 | 100 | 3500 | 10000 | 100 | 3500 | W/l
Cycle life | 10000 | 1000 | 2500 | 12030.2906 | 1203.0291 | 3007.5727 | 15157.2798 | 1515.728 | 3789.32 | 19097.0558 | 1909.7056 | 4774.264 | equivalent full-cycles
Calendar life | 20 | 5 | 12 | 22.5912 | 5.6478 | 13.5547 | 26.3073 | 6.5768 | 15.7844 | 30.6348 | 7.6587 | 18.3809 | a
Depth of discharge | 100 | 84 | 90 | 100 | 84 | 90 | 100 | 84 | 90 | 100 | 84 | 90 | %
Round-trip efficiency | 94 | 81 | 92 | 94.4927 | 81.4246 | 92.4822 | 95.1122 | 81.9584 | 93.0886 | 95.7358 | 82.4957 | 93.6989 | %
Self-discharge | 0.09 | 0.36 | 0.1 | 0.09 | 0.36 | 0.1 | 0.09 | 0.36 | 0.1 | 0.09 | 0.36 | 0.1 | % per day
Power dynamic | 0.003 | 1 | 0.01 | 0.003 | 1 | 0.01 | 0.003 | 1 | 0.01 | 0.003 | 1 | 0.01 | s to rated power
Planning & Construction Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | a
Energy installation cost | 199.5 | 840 | 577.5 | 152.2242 | 640.9439 | 440.6489 | 108.5574 | 457.0839 | 314.2452 | 77.4168 | 325.9656 | 224.1014 | USD / kWh
Power installation cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | USD / kW

## Li-Ion (Titanate) (calc) (hidden)
| Li-Ion (Titanate) | [8 empty] | Sources
|  | 2016 | 2020 | 2025 | 2030 | unit |  | Source 2016 | Source 2020 | Source 2025 | Source 2030 |  | 0.054665
| Energy installation cost | 1050 | 838.5552 | 633.0815 | 477.9557 | USD / kWh |  | ref 2016 | combination | combination | combination
| Power installation cost | 0 | 0 | 0 | 0 | USD / kW |  | ref 2016 | 1 | 1 | 1 |  | -0.047295
| Cycle life | 10000 | 12030.2906 | 15157.2798 | 19097.0558 | equivalent full-cycles |  | ref 2016 | combination | combination | combination |  | -0.030926
| Calendar life | 15 | 16.9434 | 19.7305 | 22.9761 | a |  | ref 2016 | combination | combination | combination |  | -0.0013078
| Round-trip efficiency | 96 | 96.5032 | 97.1359 | 97.7727 | % |  | ref 2016 | combination | combination | combination
interpolated
| References | [8 empty] | extrapolated
| Number of Source | Titel | Authors | Web | Date |  | Type |  |  | not needed or not available
| 1 | Technology Overview on Electricity Storage | Fuchs, Lunz, Leuthold, Sauer | http://www.sefep.eu/activities/projects-studies/120628_Technology_Overview_Electricity_Storage_SEFEP_ISEA.pdf | June 2012 |  | lithium-ion batteries
| 2 | Agora Stromspeicher in der Energiewende | Agora Energiewende | http://www.speicherinitiative.at/assets/Uploads/19-AgoraEnergiewende-Speicherstudie-Langfassung.pdf | September 2014 |  | lithium-ion batteries
| 3 | Batteriespeicher in der Nieder- und Mittelspannungsebene | VDE | http://www.speicherinitiative.at/assets/Uploads/03-Batterienspeicher.pdf | Mai 2015 |  | lithium-ion batteries
| 4 | Energiesysteme der Zukunft - Technologiesteckbrief Energiespeicher | Prof. Dr. Peter Elsner, Prof. Dr. Dirk Uwe Sauer | http://www.acatech.de/fileadmin/user_upload/Baumstruktur_nach_Website/Acatech/root/de/Publikationen/Materialien/ESYS_Technologiesteckbrief_Energiespeicher.pdf | November 2015 |  | lithium-ion batteries
| 5 | Battery Storage for Renewables: Market Status and Technology Outlook | Ruud Kempener (IRENA) and Eric Borden | http://www.irena.org/documentdownloads/publications/irena_battery_storage_report_2015.pdf | January 2015 |  | Titanate
Percental
Interpolation |  | ref | source
Source 1 |  | 2016 | 2012 | 2020 | 2023 | 2025 | 2030 | 2033 | unit | X1 | X2 | Seite | Kommentar
| Energy installation cost | 1000 | 550 | 369.6904 |  | 288.41 | 225 |  | € / kWh | 0.048444 |  | S.42
| Power installation cost | 0 | 175 | 100.2836 |  | 70.8109 | 50 |  | € / kW | 0.067231 |  | S.42
| Cycle life | 10000 | 3000 | 4230.2125 |  | 5243.6992 | 6500 |  | equivalent full-cycles | -0.043891 |  | S.42
| Calendar life | 15 | 12.5 | 15.4039 |  | 17.5521 | 20 |  | a | -0.026455 |  | S.42
| Round-trip efficiency | 96 | 84.5 | 86.255 |  | 87.3703 | 88.5 |  | % | -0.0025728 |  | S.42
Source 2 |  | 2016 | 2014 | 2020 | 2023 | 2025 | 2030 | 2033 | unit |  |  | S. 127-128
| Energy installation cost | 1000 | 550 | 406.9112 | 350 | 333.5193 | 295.6333 | 275 | € / kWh | 0.04898 | 0.023828 | S. 127-128
| Power installation cost | 0 | 160 |  | 90 |  |  | 40 | € / kW |  |  | S. 127-128
| Cycle life | 10000 | [6 empty] | equivalent full-cycles
| Calendar life | 15 | 12 | 13.9248 | 15 | 15.8884 | 18.3463 | 20 | a | -0.025104 | -0.029186 | S. 127-128
| Round-trip efficiency | 96 | 90 | 90 | 90 | 90 | 90 | 90 | % | 0 | 0 | S. 127-128
Source 3 |  | 2016 | 2015 | 2020 | 2023 | 2025 | 2030 | 2033 | unit
| Energy installation cost | 1000 | 285 | 180 |  | 145 | 116.8056 |  | € / kWh | 0.057732 | 0.042323 | S. 90 | Es gibt auch Preise von Li-Ionen-System PV Speicher (2015: 750€/kWh - 1250€/kWh 2020
| Power installation cost | 0 | 125 | 92.5 |  | 75 |  |  | € / kW |  |  | S. 95
| Cycle life | 10000 | 3000 | 5000 |  | 5916.0798 | 7000 |  | equivalent full-cycles | -0.058112 | -0.03422 | S. 61
| Calendar life | 15 | 12.5 | 20 |  | 20 | 20 |  | a | -0.03183 | 0 | S. 61
| Round-trip efficiency | 96 | 97 | 97 |  | 97 | 97 |  | % | 0 | 0 | S. 61
Source 4,X |  | 2016 | 2013 | 2020 | 2023 | 2025 | 2030 | 2050 | unit
| Energy installation cost | 1000 | 445 | 199.0496 | 141 | 138.0029 | 130.786 | 105.5 | € / kWh | 0.10857 | 0.010685 | S. 31-32 | Kosten sind für Großspeicher eingetragen, es gibt aber auch PV
| Power installation cost | 0 | 160 |  | 72.5 |  |  | 45 | € / kW |  |  | S. 31-32
| Cycle life | 10000 | 5000 | 6327.9003 | 7000 | 7285.1339 | 8049.822 | 12000 | equivalent full-cycles | -0.03422 | -0.020163 | S. 31-32
| Calendar life | 15 | 13 | 15.6855 | 17 | 17.3278 | 18.1752 | 22 | a | -0.027189 | -0.009595 | S. 31-32
| Round-trip efficiency | 96 | 85.5 | 86.5473 | 87 | 87.2188 | 87.768 | 90 | % | -0.0017407 | -0.0012564 | S. 31-32 | Sehr gering!
Source 5 |  | 2016 | 2014 | 2017 | 2020 | 2025 | 2030 | 2050 | unit
| Energy installation cost | 1050 | 800 | 650 | 600 | 472.1018 | 371.4668 |  | USD / kWh | 0.066872 | 0.046816 | S- 30
| Power installation cost | 0 | [6 empty] | USD / kW
| Cycle life | 10000 | [6 empty] | equivalent full-cycles
| Calendar life | 15 | [6 empty] | a
| Round-trip efficiency | 96 | [6 empty] | %
|  |  | price | cycle life | calender | efficiency
|  |  | 40.91% | 216.7% | 160% | 104.7%
|  |  | 53.75% | 152.9% | 152.9% | 100%
|  |  | 40.98% | 233.3% | 160% | 100%
|  |  | 29.39% | 161% | 139.8% | 102.7%
46.43%
|  |  | avg | avg | avg | avg
|  |  | 45.52% | 191% | 153.2% | 101.8%

## Li-Ion (Titanate) (hidden)
| 2016 |  |  | 2020 |  |  | 2025 |  |  | 2030
Li-Ion (Titanate) (calc) | best | worst | reference | best | worst | reference | best | worst | reference | best | worst | reference | unit
Energy density | 620 | 200 | 350 | 620 | 200 | 350 | 620 | 200 | 350 | 620 | 200 | 350 | Wh/l
Power density | 10000 | 100 | 3500 | 10000 | 100 | 3500 | 10000 | 100 | 3500 | 10000 | 100 | 3500 | W/l
Cycle life | 20000 | 5000 | 10000 | 24060.5813 | 6015.1453 | 12030.2906 | 30314.5597 | 7578.6399 | 15157.2798 | 38194.1116 | 9548.5279 | 19097.0558 | equivalent full-cycles
Calendar life | 20 | 10 | 15 | 22.5912 | 11.2956 | 16.9434 | 26.3073 | 13.1537 | 19.7305 | 30.6348 | 15.3174 | 22.9761 | a
Depth of discharge | 100 | 84 | 95 | 100 | 84 | 95 | 100 | 84 | 95 | 100 | 84 | 95 | %
Round-trip efficiency | 98 | 81 | 96 | 99 | 81.4246 | 96.5032 | 99 | 81.9584 | 97.1359 | 99 | 82.4957 | 97.7727 | %
Self-discharge | 0.09 | 0.36 | 0.05 | 0.09 | 0.36 | 0.05 | 0.09 | 0.36 | 0.05 | 0.09 | 0.36 | 0.05 | % per day
Power dynamic | 0.003 | 1 | 0.01 | 0.003 | 1 | 0.01 | 0.003 | 1 | 0.01 | 0.003 | 1 | 0.01 | s to rated power
Planning & Construction Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | a
Energy installation cost | 472.5 | 1260 | 1050 | 377.3499 | 1006.2663 | 838.5552 | 284.8867 | 759.6978 | 633.0815 | 215.0801 | 573.5468 | 477.9557 | USD / kWh
Power installation cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | USD / kW

## NaNiCl (calc) (hidden)
| NaNiCl | [8 empty] | Sources
|  | 2016 | 2020 | 2025 | 2030 | unit |  | Source 2016 | Source 2020 | Source 2025 | Source 2030 |  | 0.062629
| Energy installation cost | 399 | 308.0485 | 222.9343 | 161.3372 | USD / kWh |  | ref 2016 | combination | combination | combination
| Power installation cost | 0 | 0 | 0 | 0 | USD / kW |  | ref 2016
| Cycle life | 3000 | 3376.5264 | 3914.3196 | 4537.7692 | equivalent full-cycles |  | ref 2016
| Calendar life | 15 | 16.8826 | 19.5716 | 22.6888 | a |  | ref 2016
| Round-trip efficiency | 84 | 85 | 86 | 87 | % |  | ref 2016
Note: As no reliable data could be found, a simple estimation of 3% annual performance increase / price decrease was used as a reference. For the round-trip efficiency, an increase of 1 percent point per period was assumed.
interpolated
| References | [8 empty] | extrapolated
| Number of Source | Titel | Authors | Web | Data |  | Type |  |  | not needed or not available
| 1 | Agora Stromspeicher in der Energiewende | Agora Energiewende | http://www.speicherinitiative.at/assets/Uploads/19-AgoraEnergiewende-Speicherstudie-Langfassung.pdf | September 2014 |  | NaS/NaCl
| 2 | Battery Storage for Renewables: Market Status and Technology Outlook | Ruud Kempener (IRENA) and Eric Borden | http://www.irena.org/documentdownloads/publications/irena_battery_storage_report_2015.pdf | January 2015 |  | sodium metal halide
Percental
Interpolation |  | ref | source
Source 1 |  | 2016 | 2014 | 2020 | 2023 | 2025 | 2030 | 2033 | unit | X1 | X2
| Energy installation cost |  | 400 | 258.6001 | 250 | 179.7916 | 125 | 125 | € / kWh | 0.070117 |  | S. 127-128
| Power installation cost |  | 160 |  | 90 |  |  | 40 | € / kW |  |  | S. 127-128
| Cycle life | [7 empty] | equivalent full-cycles
| Calendar life | [7 empty] | a
| Round-trip efficiency |  | 75 |  | 75 |  |  | 75 | % |  |  | S. 127-128
Source 4 |  | 2016 | 2014 | 2017 | 2020 | 2025 | 2030 | 2050 | unit
| Energy installation cost |  | 488 | 465 | 400 | 311.223 | 242.1494 |  | USD / kWh | 0.015964 | 0.048952 | S.30
| Power installation cost |  | 0 | [5 empty] | USD / kW
| Cycle life |  | 2250 | [5 empty] | equivalent full-cycles |  |  | S. 43
| Calendar life |  | 15 | [5 empty] | a
| Round-trip efficiency |  | 84 | [5 empty] | %
|  |  | price | cycle life | calender | efficiency
31.25%
49.62%
|  |  | avg | avg | avg | avg
40.44%

## NaNiCl (hidden)
| 2016 |  |  | 2020 |  |  | 2025 |  |  | 2030
NaNiCl (calc) | best | worst | reference | best | worst | reference | best | worst | reference | best | worst | reference | unit
Energy density | 280 | 150 | 215 | 280 | 150 | 215 | 280 | 150 | 215 | 280 | 150 | 215 | Wh/l
Power density | 270 | 150 | 210 | 270 | 150 | 210 | 270 | 150 | 210 | 270 | 150 | 210 | W/l
Cycle life | 7500 | 1000 | 3000 | 8441.3161 | 1125.5088 | 3376.5264 | 9785.7989 | 1304.7732 | 3914.3196 | 11344.4229 | 1512.5897 | 4537.7692 | equivalent full-cycles
Calendar life | 22 | 8 | 15 | 24.7612 | 9.0041 | 16.8826 | 28.705 | 10.4382 | 19.5716 | 33.277 | 12.1007 | 22.6888 | a
Depth of discharge | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | %
Round-trip efficiency | 92 | 80 | 84 | 93.0952 | 80.9524 | 85 | 94.1905 | 81.9048 | 86 | 95.2857 | 82.8571 | 87 | %
Self-discharge | 0.05 | 15 | 5 | 0.05 | 15 | 5 | 0.05 | 15 | 5 | 0.05 | 15 | 5 | % per day
Power dynamic | 0.1 | < 1 | 0.5 | 0.1 | 0 | 0.5 | 0.1 | 0 | 0.5 | 0.1 | 0 | 0.5 | s to rated power
Planning & Construction Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | a
Energy installation cost | 315 | 488 | 399 | 243.1962 | 376.7611 | 308.0485 | 176.0007 | 272.6615 | 222.9343 | 127.3715 | 197.3247 | 161.3372 | USD / kWh
Power installation cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | USD / kW

## NaS (calc) (hidden)
| NaS | [8 empty] | Sources
|  | 2016 | 2020 | 2025 | 2030 | unit |  | Source 2016 | Source 2020 | Source 2025 | Source 2030 |  | 0.056839
| Energy installation cost | 367.5 | 290.8044 | 217.0354 | 161.9795 | USD / kWh |  | ref 2016 | combination | combination | combination
| Power installation cost | 0 | 0 | 0 | 0 | USD / kW |  | ref 2016 | 1 | 1 | 1 |  | -0.029385
| Cycle life | 5000 | 5614.1213 | 6488.9067 | 7500 | equivalent full-cycles |  | ref 2016 | combination | combination | combination |  | -0.025804
| Calendar life | 17 | 18.8238 | 21.381 | 24.2857 | a |  | ref 2016 | combination | combination | combination |  | -0.0043397
| Round-trip efficiency | 80 | 81.3978 | 83.1794 | 85 | % |  | ref 2016 | combination | combination | combination
interpolated
| References | [8 empty] | extrapolated
| Number of Source | Titel | Authors | Web | Data |  | Type |  |  | not needed or not available
| 1 | Technology Overview on Electricity Storage | Fuchs, Lunz, Leuthold, Sauer | http://www.sefep.eu/activities/projects-studies/120628_Technology_Overview_Electricity_Storage_SEFEP_ISEA.pdf | June 2012 |  | High temperature batteries (NaS)
| 2 | Agora Stromspeicher in der Energiewende | Agora Energiewende | http://www.speicherinitiative.at/assets/Uploads/19-AgoraEnergiewende-Speicherstudie-Langfassung.pdf | September 2014 |  | NaS/NaCl
| 3 | Energiesysteme der Zukunft - Technologiesteckbrief Energiespeicher | Prof. Dr. Peter Elsner, Prof. Dr. Dirk Uwe Sauer | http://www.speicherinitiative.at/assets/Uploads/03-Batterienspeicher.pdf | November 2015 |  | sodium sulphur batteries
| 4 | Battery Storage for Renewables: Market Status and Technology Outlook | Ruud Kempener (IRENA) and Eric Borden | http://www.irena.org/documentdownloads/publications/irena_battery_storage_report_2015.pdf | January 2015 |  | sodium sulphur
Percental
Interpolation |  | ref | source
Source 1 |  | 2016 | 2012 | 2020 | 2023 | 2025 | 2030 | 2033 | unit | X1 | X2 | Seite | Kommentar | Tabelle
| Energy installation cost | 350 | 600 | 287.9274 |  | 181.9661 | 115 |  | € / kWh | 0.087692 |  | S.47
| Power installation cost | 0 | 175 | 100.2836 |  | 70.8109 | 50 |  | € / kW | 0.067231 |  | S.47
| Cycle life | 5000 | 7500 | 7500 |  | 7500 | 7500 |  | equivalent full-cycles | 0 |  | S.47
| Calendar life | 17 | 17.5 | 20.5061 |  | 22.6418 | 25 |  | a | -0.020013 |  | S.47
| Round-trip efficiency | 80 | 77.5 | 80.748 |  | 82.8467 | 85 |  | % | -0.005145 |  | S.47
Source 2 |  | 2016 | 2014 | 2020 | 2023 | 2025 | 2030 | 2033 | unit
| Energy installation cost | 350 | 400 | 292.4018 | 250 | 217.6376 | 153.8931 | 125 | USD / kWh | 0.050882 | 0.066967 | S. 127-128
| Power installation cost | 0 | 160 |  | 90 |  |  | 40 | USD / kW |  |  | S. 127-128
| Cycle life | 5000 | [6 empty] | equivalent full-cycles
| Calendar life | 17 | [6 empty] | a
| Round-trip efficiency | 80 | 75 | 75 | 75 | 75 | 75 | 75 | % | 0 | 0 | S. 127-128
Source 3 |  | 2016 |  | 2020 | 2023 | 2025 | 2030 | 2050 | unit
Source 4 |  | 2016 | 2014 | 2017 | 2020 | 2025 | 2030 | 2050 | unit
| Energy installation cost | 367.5 | 535 | 535 | 500 | 446.6805 | 399.047 |  | USD / kWh | 0 | 0.0223 | S.30
| Power installation cost | 0 | [6 empty] | USD / kW
| Cycle life | 5000 | 2250 | [5 empty] | equivalent full-cycles |  |  | S. 43
| Calendar life | 17 | [6 empty] | a
| Round-trip efficiency | 80 | [6 empty] | %
|  |  | price | cycle life | calender | efficiency
|  |  | 19.17% | 100% | 142.9% | 109.7%
|  |  | 38.47% |  |  | 100%
74.59%
|  |  | avg | avg | avg | avg
|  |  | 44.08% | 100% | 142.9% | 104.8%

## NaS (hidden)
| 2016 |  |  | 2020 |  |  | 2025 |  |  | 2030
NaS (calc) | best | worst | reference | best | worst | reference | best | worst | reference | best | worst | reference | unit
Energy density | 300 | 140 | 250 | 300 | 140 | 250 | 300 | 140 | 250 | 300 | 140 | 250 | Wh/l
Power density | 160 | 120 | 140 | 160 | 120 | 140 | 160 | 120 | 140 | 160 | 120 | 140 | W/l
Cycle life | 10000 | 1000 | 5000 | 11228.2426 | 1122.8243 | 5614.1213 | 12977.8133 | 1297.7813 | 6488.9067 | 15000 | 1500 | 7500 | equivalent full-cycles
Calendar life | 25 | 10 | 17 | 27.682 | 11.0728 | 18.8238 | 31.4427 | 12.5771 | 21.381 | 35.7143 | 14.2857 | 24.2857 | a
Depth of discharge | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | %
Round-trip efficiency | 90 | 70 | 80 | 91.5725 | 71.2231 | 81.3978 | 93.5768 | 72.782 | 83.1794 | 95.625 | 74.375 | 85 | %
Self-discharge | 0.05 | 1 | 0.05 | 0.05 | 1 | 0.05 | 0.05 | 1 | 0.05 | 0.05 | 1 | 0.05 | % per day
Power dynamic | 3 | 20 | 10 | 3 | 20 | 10 | 3 | 20 | 10 | 3 | 20 | 10 | s to rated power
Planning & Construction Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | a
Energy installation cost | 262.5 | 735 | 367.5 | 207.7174 | 581.6088 | 290.8044 | 155.0253 | 434.0707 | 217.0354 | 115.6996 | 323.959 | 161.9795 | USD / kWh
Power installation cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | USD / kW

## Vanadium Flow (calc) (hidden)
| Vanadium Flow | [8 empty] | Sources
|  | 2016 | 2020 | 2025 | 2030 | unit |  | Source 2016 | Source 2020 | Source 2025 | Source 2030 |  | 0.073589
| Energy installation cost | 346.5 | 255.2215 | 174.1546 | 118.8372 | USD / kWh |  | ref 2016 | combination | combination | combination |  | 0.051157
| Power installation cost | 1312.5 | 1063.8428 | 818.1823 | 629.2493 | USD / kW |  | ref 2016 | 1 | 1 | 1 |  | 0
| Cycle life | 13000 | 13000 | 13000 | 13000 | equivalent full-cycles |  | ref 2016 | combination | combination | combination |  | -0.034142
| Calendar life | 12 | 13.7246 | 16.2331 | 19.2 | a |  | ref 2016 | combination | combination | combination |  | -0.0078304
| Round-trip efficiency | 70 | 72.2184 | 75.0906 | 78.0769 | % |  | ref 2016 | combination | combination | combination
interpolated
| References | [8 empty] | extrapolated
| Number of Source | Titel | Authors | Web | Data |  | Type |  |  | not needed or not available
| 1 | Technology Overview on Electricity Storage | Fuchs, Lunz, Leuthold, Sauer | http://www.sefep.eu/activities/projects-studies/120628_Technology_Overview_Electricity_Storage_SEFEP_ISEA.pdf | June 2012 |  | flow batteries
| 2 | Agora Stromspeicher in der Energiewende | Agora Energiewende | http://www.speicherinitiative.at/assets/Uploads/19-AgoraEnergiewende-Speicherstudie-Langfassung.pdf | September 2014 |  | redox flow batteries
| 3 | Energiesysteme der Zukunft - Technologiesteckbrief Energiespeicher | Prof. Dr. Peter Elsner, Prof. Dr. Dirk Uwe Sauer | http://www.speicherinitiative.at/assets/Uploads/03-Batterienspeicher.pdf | November 2015 |  | redox flow batteries
| 4 | Battery Storage for Renewables: Market Status and Technology Outlook | Ruud Kempener (IRENA) and Eric Borden | http://www.irena.org/documentdownloads/publications/irena_battery_storage_report_2015.pdf | January 2015 |  | flow batteries
Percental
Interpolation |  | ref | source
Source 1 |  | 2016 | 2012 | 2020 | 2023 | 2025 | 2030 | 2033 | unit | X1 | X2 | Seite | Kommentar | Tabelle
| Energy installation cost | 330 | 400 | 225.3588 |  | 157.4467 | 110 |  | € / kWh | 0.06921 |  | S.39
| Power installation cost | 1250 | 1250 | 1025.1036 |  | 1000 | 800 |  | € / kW | 0.024489 |  | S.39
| Cycle life | 13000 | 10000 | 10000 |  | 13000 | 10000 |  | equivalent full-cycles | 0 |  | S.39
| Calendar life | 12 | 12.5 | 15.4039 |  | 15.1789 | 20 |  | a | -0.026455 |  | S.39
| Round-trip efficiency | 70 | 65 | 68.2325 |  | 73.9282 | 72.5 |  | % | -0.0060851 |  | S.39
Source 2 |  | 2016 | 2014 | 2020 | 2023 | 2025 | 2030 | 2033 | unit
| Energy installation cost | 330 | 900 | 608.2202 | 500 | 458.7253 | 369.8361 | 325 | € / kWh | 0.063223 | 0.042164 | S. 127-128
| Power installation cost | 1250 | 160 | 109.0272 | 90 | 76.5255 | 51.017 | 40 | € / kW | 0.061929 | 0.077892 | S. 127-128
| Cycle life | 13000 | [6 empty] | equivalent full-cycles
| Calendar life | 12 | [6 empty] | a
| Round-trip efficiency | 70 | 65 | 65 | 65 | 65 | 65 | 65 | % | 0 | 0 | S. 127-128
Source 3 |  | 2016
| Energy installation cost | 330
| Power installation cost | 1250
| Cycle life | 13000
| Calendar life | 12
| Round-trip efficiency | 70
Source 4 |  | 2016 | 2014 | 2017 | 2020 | 2025 | 2030 | 2050 | unit
| Energy installation cost | 346.5 | 680 | 550 | 350 | 164.7822 | 77.5805 |  | USD / kWh | -0.5873 | 0.13986 | S. 30
| Power installation cost | 1312.5 | [6 empty] | USD / kW
| Cycle life | 13000 | [6 empty] | equivalent full-cycles
| Calendar life | 12 | [6 empty] | a
| Round-trip efficiency | 70 | [6 empty] | %
|  |  | price | cycle life | calender | efficiency | power
|  |  | 27.5% | 100% | 160% | 111.5% | 64%
|  |  | 41.09% |  |  |  | 31.89%
11.41%
|  |  | avg | avg | avg | avg | avg
|  |  | 34.3% | 100% | 160% | 111.5% | 47.94%

## Vanadium Flow (hidden)
| 2016 |  |  | 2020 |  |  | 2025 |  |  | 2030
Vanadium Flow (calc) | best | worst | reference | best | worst | reference | best | worst | reference | best | worst | reference | unit
Energy density | 70 | 15 | 45 | 70 | 15 | 45 | 70 | 15 | 45 | 70 | 15 | 45 | Wh/l
Power density | 2 | 0.5 | 1.3 | 2 | 0.5 | 1.3 | 2 | 0.5 | 1.3 | 2 | 0.5 | 1.3 | W/l
Cycle life | 14000 | 12000 | 13000 | 14000 | 12000 | 13000 | 14000 | 12000 | 13000 | 14000 | 12000 | 13000 | equivalent full-cycles
Calendar life | 20 | 5 | 12 | 22.8744 | 5.7186 | 13.7246 | 27.0552 | 6.7638 | 16.2331 | 32 | 8 | 19.2 | a
Depth of discharge | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | %
Round-trip efficiency | 85 | 60 | 70 | 87.6938 | 61.9015 | 72.2184 | 91.1814 | 64.3633 | 75.0906 | 94.8077 | 66.9231 | 78.0769 | %
Self-discharge | 0 | 1 | 0.15 | 0 | 1 | 0.15 | 0 | 1 | 0.15 | 0 | 1 | 0.15 | % per day
Power dynamic | < 0.001 | 0.02 | 0.01 | 0 | 0.02 | 0.01 | 0 | 0.02 | 0.01 | 0 | 0.02 | 0.01 | s to rated power
Planning & Construction Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | a
Energy installation cost | 315 | 1050 | 346.5 | 232.0196 | 773.3986 | 255.2215 | 158.3223 | 527.7411 | 174.1546 | 108.0338 | 360.1128 | 118.8372 | USD / kWh
Power installation cost | 1050 | 1575 | 1312.5 | 851.0742 | 1276.6113 | 1063.8428 | 654.5459 | 981.8188 | 818.1823 | 503.3995 | 755.0992 | 629.2493 | USD / kW

## ZnBr Flow (calc) (hidden)
| Zn/Br Flow | [8 empty] | Sources
|  | 2016 | 2020 | 2025 | 2030 | unit |  | Source 2016 | Source 2020 | Source 2025 | Source 2030 |  | 0.073589
| Energy installation cost | 900 | 662.913 | 452.3495 | 308.6681 | USD / kWh |  | ref 2016 | combination | combination | combination
| Power installation cost | 0 | 0 | 0 | 0 | USD / kW |  | ref 2016 | 1 | 1 | 1 |  | 0
| Cycle life | 10000 | 10000 | 10000 | 10000 | equivalent full-cycles |  | ref 2016 | combination | combination | combination |  | -0.034142
| Calendar life | 10 | 11.4372 | 13.5276 | 16 | a |  | ref 2016 | combination | combination | combination |  | -0.0078304
| Round-trip efficiency | 70 | 72.2184 | 75.0906 | 78.0769 | % |  | ref 2016 | combination | combination | combination
interpolated
| References | [8 empty] | extrapolated
| Number of Source | Titel | Authors | Web | Data |  | Type |  |  | not needed or not available
| 1 | Technology Overview on Electricity Storage | Fuchs, Lunz, Leuthold, Sauer | http://www.sefep.eu/activities/projects-studies/120628_Technology_Overview_Electricity_Storage_SEFEP_ISEA.pdf | June 2012 |  | flow batteries
| 2 | Agora Stromspeicher in der Energiewende | Agora Energiewende | http://www.speicherinitiative.at/assets/Uploads/19-AgoraEnergiewende-Speicherstudie-Langfassung.pdf | September 2014 |  | redox flow batteries
| 3 | Energiesysteme der Zukunft - Technologiesteckbrief Energiespeicher | Prof. Dr. Peter Elsner, Prof. Dr. Dirk Uwe Sauer | http://www.speicherinitiative.at/assets/Uploads/03-Batterienspeicher.pdf | November 2015 |  | redox flow batteries
| 4 | Battery Storage for Renewables: Market Status and Technology Outlook | Ruud Kempener (IRENA) and Eric Borden | http://www.irena.org/documentdownloads/publications/irena_battery_storage_report_2015.pdf | January 2015 |  | flow batteries
Percental
Interpolation |  | ref | source
Source 1 |  | 2016 | 2012 | 2020 | 2023 | 2025 | 2030 | 2033 | unit | X1 | X2 | Seite | Kommentar | Tabelle
| Energy installation cost | 857.1429 | 400 | 225.3588 |  | 157.4467 | 110 |  | € / kWh | 0.06921 |  | S.39
| Power installation cost | 0 | 1250 | 1025.1036 |  | 0 | 800 |  | € / kW | 0.024489 |  | S.39
| Cycle life | 10000 | 10000 | 10000 |  | 10000 | 10000 |  | equivalent full-cycles | 0 |  | S.39
| Calendar life | 10 | 12.5 | 15.4039 |  | 12.6491 | 20 |  | a | -0.026455 |  | S.39
| Round-trip efficiency | 70 | 65 | 68.2325 |  | 73.9282 | 72.5 |  | % | -0.0060851 |  | S.39
Source 2 |  | 2016 | 2014 | 2020 | 2023 | 2025 | 2030 | 2033 | unit
| Energy installation cost | 857.1429 | 900 | 608.2202 | 500 | 458.7253 | 369.8361 | 325 | € / kWh | 0.063223 | 0.042164 | S. 127-128
| Power installation cost | 0 | 160 | 109.0272 | 90 | 76.5255 | 51.017 | 40 | € / kW | 0.061929 | 0.077892 | S. 127-128
| Cycle life | 10000 | [6 empty] | equivalent full-cycles
| Calendar life | 10 | [6 empty] | a
| Round-trip efficiency | 70 | 65 | 65 | 65 | 65 | 65 | 65 | % | 0 | 0 | S. 127-128
Source 3 |  | 2016
| Energy installation cost | 857.1429
| Power installation cost | 0
| Cycle life | 10000
| Calendar life | 10
| Round-trip efficiency | 70
Source 4 |  | 2016 | 2014 | 2017 | 2020 | 2025 | 2030 | 2050 | unit
| Energy installation cost | 900 | 680 | 550 | 350 | 164.7822 | 77.5805 |  | USD / kWh | 0.38889 | 0.13986 | S. 30
| Power installation cost | 0 | [6 empty] | USD / kW
| Cycle life | 10000 | [6 empty] | equivalent full-cycles
| Calendar life | 10 | [6 empty] | a
| Round-trip efficiency | 70 | [6 empty] | %
|  |  | price | cycle life | calender | efficiency | power
|  |  | 27.5% | 100% | 160% | 111.5% | 64%
|  |  | 41.09% |  |  |  | 31.89%
11.41%
|  |  | avg | avg | avg | avg | avg
|  |  | 34.3% | 100% | 160% | 111.5% | 47.94%

## ZnBr Flow (hidden)
| 2016 |  |  | 2020 |  |  | 2025 |  |  | 2030
ZnBr Flow (calc) | best | worst | reference | best | worst | reference | best | worst | reference | best | worst | reference | unit
Energy density | 70 | 20 | 45 | 70 | 20 | 45 | 70 | 20 | 45 | 70 | 20 | 45 | Wh/l
Power density | 25 | 0.5 | 10 | 25 | 0.5 | 10 | 25 | 0.5 | 10 | 25 | 0.5 | 10 | W/l
Cycle life | 14000 | 300 | 10000 | 14000 | 300 | 10000 | 14000 | 300 | 10000 | 14000 | 300 | 10000 | equivalent full-cycles
Calendar life | 20 | 5 | 10 | 22.8744 | 5.7186 | 11.4372 | 27.0552 | 6.7638 | 13.5276 | 32 | 8 | 16 | a
Depth of discharge | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | %
Round-trip efficiency | 85 | 60 | 70 | 87.6938 | 61.9015 | 72.2184 | 91.1814 | 64.3633 | 75.0906 | 94.8077 | 66.9231 | 78.0769 | %
Self-discharge | 8 | 33.6 | 15 | 8 | 33.6 | 15 | 8 | 33.6 | 15 | 8 | 33.6 | 15 | % per day
Power dynamic | < 0.001 | 0.02 | 0.01 | 0 | 0.02 | 0.01 | 0 | 0.02 | 0.01 | 0 | 0.02 | 0.01 | s to rated power
Planning & Construction Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | a
Energy installation cost | 525 | 1680 | 900 | 386.6993 | 1237.4377 | 662.913 | 263.8706 | 844.3858 | 452.3495 | 180.0564 | 576.1804 | 308.6681 | USD / kWh
Power installation cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | USD / kW

## Inverter small (calc) (hidden)
| Inverter small | [8 empty] | Sources
|  | 2016 | 2020 | 2025 | 2030 | unit |  | Source 2016 | Source 2020 | Source 2025 | Source 2030
| Energy installation cost |  |  |  |  | USD / kWh | [6 empty] | 0.064944
| Power installation cost | 155.4 | 118.7961 | 84.9163 | 60.6987 | USD / kW |  | ref 2016 | combination | combination | combination
| Cycle life |  | 0 | 0 |  | equivalent full-cycles | [6 empty] | -0.036908
| Calendar life | 12 | 13.8721 | 16.6281 | 19.9317 | a |  | ref 2016 | 1 | 1 | 1 |  | 0
| Round-trip efficiency | 95 | 95 | 95 | 95 | % |  | ref 2016
interpolated
| References | [8 empty] | extrapolated
| Number of Source | Titel | Authors | Web | Data |  | specific size |  |  | not needed or not available
| 1 | Expert Guess ISEA |  |  | October 2014 |  | no
| 2 | Energiesysteme der Zukunft - Technologiesteckbrief Energiespeicher | Prof. Dr. Peter Elsner, Prof. Dr. Dirk Uwe Sauer | http://www.acatech.de/fileadmin/user_upload/Baumstruktur_nach_Website/Acatech/root/de/Publikationen/Materialien/ESYS_Technologiesteckbrief_Energiespeicher.pdf | November 2015 |  | no
| 3 | Batteriespeicher in der Nieder- und Mittelspannungsebene | VDE | http://www.speicherinitiative.at/assets/Uploads/03-Batterienspeicher.pdf | Mai 2015 |  | "stationary systems"
| 4 | ISEA estimation |  |  | 2015 |  | home storage systems
Percental
Interpolation |  | ref | source
Source 1 |  | 2016 |  | 2020 | 2024 | 2025 | 2030 | 2034 | unit | X1 | X2
| Energy installation cost | [7 empty] | USD / kWh
| Power installation cost | 148 |  | 103.9423 | 73 | 69.8555 | 56.0516 | 47 | USD / kW | 0.084554 | 0.043076
| Cycle life | [7 empty] | equivalent full-cycles
| Calendar life | 12 |  | 18 | 27 | 27.4626 | 29.8975 | 32 | a | -0.10668 | -0.017135
| Round-trip efficiency | [7 empty] | %
Source 2 |  | 2016 | 2013 | 2020 | 2023 | 2025 | 2030 | 2050 | unit
| Energy installation cost | [7 empty] | € / kWh
| Power installation cost | 148 | 160 | 92.3766 | 73 | 70.4302 | 64.3947 | 45 | € / kW | 0.075472 | 0.017759 | S.32
| Cycle life | [7 empty] | equivalent full-cycles
| Calendar life | [7 empty] | a
| Round-trip efficiency | [7 empty] | %
Source 3 |  | 2016 | 2015 | 2020 | 2023 | 2025 | 2030 | 2050 | unit
| Energy installation cost | [7 empty] | € / kWh
| Power installation cost | 148 | 125 | 92.5 |  | 75 | 60.8108 |  | € / kW |  | 0.041077 | S.95
| Cycle life | [7 empty] | equivalent full-cycles
| Calendar life | [7 empty] | a
| Round-trip efficiency | [7 empty] | %
Source 4 |  | 2016 |  | 2020 | 2023 | 2025 | 2030 | 2050 | unit
| Energy installation cost | [7 empty] | USD / kWh
| Power installation cost | 148 |  | 95 |  | 69 | 53 |  | USD / kW
| Cycle life | [7 empty] | equivalent full-cycles
| Calendar life | [7 empty] | a
| Round-trip efficiency | [7 empty] | %
|  |  | price | cycle life | calender | efficiency
|  |  | 37.87% |  | 166.1%
40.25%
48.65%
35.81%
|  |  | avg | avg | avg | avg
|  |  | 39.06% |  | 166.1%

## Inverter small (hidden)
| 2016 |  |  | 2020 |  |  | 2025 |  |  | 2030
Inverter small (calc) | best | worst | reference | best | worst | reference | best | worst | reference | best | worst | reference | unit
Energy density | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | Wh/l
Power density | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0 | 0 | 0.15 | W/l
Cycle life | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | equivalent full-cycles
Calendar life | 25 | 10 | 12 | 25 | 11.5601 | 13.8721 | 25 | 13.8568 | 16.6281 | 25 | 16.6097 | 19.9317 | a
Depth of discharge | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | %
Round-trip efficiency | 97 | 93 | 95 | 97 | 93 | 95 | 97 | 93 | 95 | 97 | 93 | 95 | %
Self-discharge | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 | 0 | 0.01 | % per day
Power dynamic | - | - | 0.02 | 0 | 0 | 0.02 | 0 | 0 | 30 | 0 | 0 | 30 | s to rated power
Planning & Construction Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 0 | 0 | - | a
Energy installation cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | USD / kWh
Power installation cost | 105 | 290 | 155.4 | 80.2676 | 221.6915 | 118.7961 | 57.3758 | 158.4666 | 84.9163 | 41.0127 | 113.2731 | 60.6987 | USD / kW

## Inverter large (calc) (hidden)
| Inverter large | [8 empty] | Sources
|  | 2016 | 2020 | 2025 | 2030 | unit |  | Source 2016 | Source 2020 | Source 2025 | Source 2030
| Energy installation cost |  |  |  |  | USD / kWh | [6 empty] | 0.050866
| Power installation cost | 105 | 85.2119 | 65.6355 | 50.5566 | USD / kW |  | ref 2016 | combination | combination | combination
| Cycle life |  |  |  |  | equivalent full-cycles | [6 empty] | -0.028677
| Calendar life | 15 | 16.7961 | 19.3466 | 22.2843 | a |  | ref 2016 | 1 | 1 | 1 |  | 0
| Round-trip efficiency | 98 | 98 | 98 | 98 | % |  | ref 2016
interpolated
| References | [8 empty] | extrapolated
| Number of Source | Titel | Authors | Web | Data |  | specific size |  |  | not needed or not available
| 1 | Expert Guess ISEA |  |  | October 2014 |  | no
| 2 | Energiesysteme der Zukunft - Technologiesteckbrief Energiespeicher | Prof. Dr. Peter Elsner, Prof. Dr. Dirk Uwe Sauer | http://www.acatech.de/fileadmin/user_upload/Baumstruktur_nach_Website/Acatech/root/de/Publikationen/Materialien/ESYS_Technologiesteckbrief_Energiespeicher.pdf | November 2015 |  | no
| 3 | Batteriespeicher in der Nieder- und Mittelspannungsebene | VDE | http://www.speicherinitiative.at/assets/Uploads/03-Batterienspeicher.pdf | Mai 2015 |  | "stationary systems"
| 4 | ISEA estimation |  |  | 2015 |  | home storage systems
Percental
Interpolation |  | ref | source
Source 1 |  | 2016 |  | 2020 | 2024 | 2025 | 2030 | 2034 | unit | X1 | X2
| Energy installation cost | [7 empty] | USD / kWh
| Power installation cost | 100 |  | 85.44 | 73 | 69.8555 | 56.0516 | 47 | USD / kW | 0.038575 | 0.043076
| Cycle life | [7 empty] | equivalent full-cycles
| Calendar life | 15 |  | 20.1246 | 27 | 27.4626 | 29.8975 | 32 | a | -0.07624 | -0.017135
| Round-trip efficiency | [7 empty] | %
Source 2 |  | 2016 | 2013 | 2020 | 2023 | 2025 | 2030 | 2050 | unit
| Energy installation cost | [7 empty] | € / kWh
| Power installation cost | 100 | 160 | 92.3766 | 73 | 70.4302 | 64.3947 | 45 | € / kW | 0.075472 | 0.017759 | S.32
| Cycle life | [7 empty] | equivalent full-cycles
| Calendar life | [7 empty] | a
| Round-trip efficiency | [7 empty] | %
Source 3 |  | 2016 | 2015 | 2020 | 2023 | 2025 | 2030 | 2050 | unit
| Energy installation cost | [7 empty] | € / kWh
| Power installation cost | 100 | 125 | 92.5 |  | 75 | 60.8108 |  | € / kW |  | 0.041077 | S.95
| Cycle life | [7 empty] | equivalent full-cycles
| Calendar life | [7 empty] | a
| Round-trip efficiency | [7 empty] | %
Source 4 |  | 2016 |  | 2020 | 2023 | 2025 | 2030 | 2050 | unit
| Energy installation cost | [7 empty] | USD / kWh
| Power installation cost | 100 |  | 95 |  | 69 | 53 |  | USD / kW
| Cycle life | [7 empty] | equivalent full-cycles
| Calendar life | [7 empty] | a
| Round-trip efficiency | [7 empty] | %
|  |  | price | cycle life | calender | efficiency
|  |  | 56.05% |  | 148.6%
40.25%
48.65%
53%
|  |  | avg | avg | avg | avg
|  |  | 48.15% |  | 148.6%

## Inverter large (hidden)
| 2016 |  |  | 2020 |  |  | 2025 |  |  | 2030
Inverter large (calc) | best | worst | reference | best | worst | reference | best | worst | reference | best | worst | reference | unit
Energy density | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | Wh/l
Power density | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0 | 0 | 0.15 | W/l
Cycle life | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | equivalent full-cycles
Calendar life | 25 | 12 | 15 | 25 | 13.4369 | 16.7961 | 25 | 15.4772 | 19.3466 | 25 | 17.8275 | 22.2843 | a
Depth of discharge | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | %
Round-trip efficiency | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | %
Self-discharge | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | % per day
Power dynamic | - | - | 0.02 | 0 | 0 | 0.02 | 0 | 0 | 30 | 0 | 0 | 30 | s to rated power
Planning & Construction Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 0 | 0 | - | a
Energy installation cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | USD / kWh
Power installation cost | 73.5 | 189 | 105 | 59.6483 | 153.3814 | 85.2119 | 45.9449 | 118.1439 | 65.6355 | 35.3896 | 91.0018 | 50.5566 | USD / kW

## No Inverter (hidden)
| 2016 |  |  | 2020 |  |  | 2025 |  |  | 2030
No inverter | best | worst | reference | best | worst | reference | best | worst | reference | best | worst | reference | unit
Energy density | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Wh/l
Power density | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | W/l
Cycle life | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | equivalent full-cycles
Calendar life | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | a
Depth of discharge | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | %
Round-trip efficiency | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | %
Self-discharge | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | % per day
Power dynamic | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | s to rated power
Planning & Construction Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | a
Energy installation cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | USD / kWh
Power installation cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | USD / kW

## Generator PHS (hidden)
| 2016 |  |  | 2020 |  |  | 2025 |  |  | 2030
Generator PHS | best | worst | reference | best | worst | reference | best | worst | reference | best | worst | reference | unit
Energy density | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Wh/l
Power density | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | W/l
Cycle life | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | equivalent full-cycles
Calendar life | 80 | 40 | 50 | 80 | 40 | 50 | 80 | 40 | 50 | 80 | 40 | 50 | a
Depth of discharge | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | %
Round-trip efficiency | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | %
Self-discharge | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | % per day
Power dynamic | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | s to rated power
Planning & Construction Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | a
Energy installation cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | USD / kWh
Power installation cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | USD / kW
Please note: Only change the Calendar life in this sheet - all other values are references and need to stay that way.

## Generator CAES (hidden)
| 2016 |  |  | 2020 |  |  | 2025 |  |  | 2030
Generator CAES | best | worst | reference | best | worst | reference | best | worst | reference | best | worst | reference | unit
Energy density | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Wh/l
Power density | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | W/l
Cycle life | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | equivalent full-cycles
Calendar life | 80 | 40 | 50 | 80 | 40 | 50 | 80 | 40 | 50 | 80 | 40 | 50 | a
Depth of discharge | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | %
Round-trip efficiency | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | %
Self-discharge | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | % per day
Power dynamic | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | s to rated power
Planning & Construction Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | a
Energy installation cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | USD / kWh
Power installation cost | 400 | 1050 | 945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | USD / kW
Please note: Only change the Calendar life in this sheet - all other values are references and need to stay that way.

## Generator Flywheel (hidden)
| 2016 |  |  | 2020 |  |  | 2025 |  |  | 2030
Generator Flywheel | best | worst | reference | best | worst | reference | best | worst | reference | best | worst | reference | unit
Energy density | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Wh/l
Power density | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | W/l
Cycle life | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | equivalent full-cycles
Calendar life | 25 | 15 | 20 | 80 | 40 | 50 | 80 | 40 | 50 | 80 | 40 | 50 | a
Depth of discharge | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | %
Round-trip efficiency | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | %
Self-discharge | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | % per day
Power dynamic | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | s to rated power
Planning & Construction Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | a
Energy installation cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | USD / kWh
Power installation cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | USD / kW
Please note: Only change the Calendar life in this sheet - all other values are references and need to stay that way.